## T1,380V，50Hz
Model |  |  | MGB-F25W/RN1 | MGB-D25W/RN1 | MGB-F30W/RN1 | MGB-D30W/RN1 | MGCSL-F30W/RN1 | MGCSL-D30W/RN1 | MGCL-F30W/RN1 | MGCL-D30W/RN1 | MGB-F55W/RN1 | MGB-F60W/RN1 | MGB-F65W/RN1 | MGB-D65W/RN1 | MGBL-F65W/RN1 | MGBL-D65W/RN1 | MGB-F130W/RN1 | MGBL-F130W/RN1 | MGB-F200W/RN1 | MGBL-F200W/RN1 | MGBT-F250W/RN1 | MGBL-F250W/RN1
Cooling Capacity |  | kW | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 60 | 65 | 65 | 65 | 65 | 130 | 130 | 185 | 185 | 250 | 250
Heating Capacity |  | kW | 29.5 | 29.5 | 32 | 32 | 32 | 32 | 32 | 32 | 59 | 64 | 69 | 69 | 69 | 69 | 138 | 138 | 200 | 200 | 270 | 270
Power input | Cooling | kW | 9.3 | 9.3 | 10 | 10 | 10+1.2(Pump) | 10+1.2(Pump) | 10 | 10 | 17.5 | 19.3 | 20.4 | 20.4 | 20.4 | 20.4 | 40.8 | 40.8 | 63 | 63 | 78.3 | 78.3
| Cooling rated current | A | 14.6 | 14.6 | 16.3 | 16.3 | 18.3 | 18.3 | 16.3 | 16.3 | 30.5 | 33.6 | 36.5 | 36.5 | 36.5 | 36.5 | 73 | 73 | 110 | 110 | 141.9 | 141.9
| Heating | kW | 9.2 | 9.2 | 9.8 | 9.8 | 9.8+1.2(Pump) | 9.8+1.2(Pump) | 9.8 | 9.8 | 18.3 | 19.8 | 21.5 | 21.5 | 21.5 | 21.5 | 43 | 43 | 61 | 61 | 80 | 80
| Heating rated current | A | 14.3 | 14.3 | 16 | 16 | 17.8 | 17.8 | 16 | 16 | 31.5 | 34.3 | 37.2 | 37.2 | 37.2 | 37.2 | 74.4 | 74.4 | 107 | 107 | 146 | 146
Power supply |  | V/Ph/Hz | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-400/3/50 | 380-400/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50 | 380-415/3/50
Power supply | Manual switch | A | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 200 | 200 | 300 | 300 | 450 | 450
| Fuse | A | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 70 | 70 | 70 | 70 | 70 | 70 | 150 | 150 | 200 | 200 | 300 | 300
Max. input consumption |  | kW | 12.6 | 12.5 | 12.6 | 12.5 | 13.4 | 13.4 | 12.6 | 12.5 | 28.2 | 28.2 | 28.2 | 27.5 | 27.9 | 27.1 | 55.5 | 55.5 | 78.3 | 78.3 | 104.9 | 104.9
Max. running current |  | A | 24 | 24 | 24 | 24 | 25.3 | 25.3 | 21.1 | 21.1 | 49.8 | 49.8 | 54.5 | 54.5 | 54.5 | 54.5 | 109 | 109 | 150 | 150 | 200 | 200
Max. starting current |  | A | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 200 | 200 | 200 | 200 | 200 | 200 | 252 | 252 | 312 | 312 | 344 | 344
Compressor | Type |  | Scroll (fixed speed) | Scroll (digital+fixed speed) | Scroll (fixed speed) | Scroll (digital+fixed speed) | Scroll (fixed speed) | Scroll (digital+fixed speed) | Scroll (fixed speed) | Scroll (digital+fixed speed) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed+digital) | Scroll (fixed speed) | Scroll (fixed speed+digital) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed) | Scroll (fixed speed)
| Brand |  | Copeland | Copeland | Copeland | Copeland | Copeland | Copeland | Copeland | Copeland | Danfoss | Danfoss | Danfoss | Copeland | Danfoss | Copeland | Danfoss | Danfoss | Danfoss | Danfoss | Danfoss | Danfoss
| Model |  | ZP67KCE-TFD-522 | ZPD67KCE-TFD-532/ ZP67KCE-TFD-522 | ZP67KCE-TFD-522 | ZPD67KCE-TFD-532/ ZP67KCE-TFD-522 | ZP67KCE-TFD-522 | ZPD67KCE-TFD-532/ ZP67KCE-TFD-522 | ZP67KCE-TFD-522 | ZPD67KCE-TFD-532/ ZP67KCE-TFD-522 | SH140A4ALC | SH140A4ALC | SH140A4ALC | ZP144KCE-TFD-522 / ZPD72KCE-TFD-433 / ZP67KCE-TFD-420 | SH140A4ALC | ZP144KCE-TFD-522 / ZPD72KCE-TFD-433 / ZP67KCE-TFD-420 | SH140A4ALC | SH140A4ALC | SH140A4ALC | SH140A4ALC | SH120A4ALC | SH120A4ALC
| Quantity | Pieces | 2 | 1/1 | 2 | 1/1 | 2 | 1/1 | 2 | 1/1 | 2 | 2 | 2 | 3 | 2 | 3 | 4 | 4 | 6 | 6 | 8 | 8
| Capacity | kW | 16.2 | 16.2/16.2 | 16.2 | 16.2/16.2 | 16.2 | 16.2/16.2 | 16.2 | 16.2/16.2 | 34.7 | 34.7 | 34.7 | 35.4/16.9/16.2 | 34.7 | 35.4/16.848/16.2 | 34.7 | 34.7 | 34.7 | 34.7 | 32.6 | 32.6
| Input | kW | 5.2 | 5.26/5.2 | 5.2 | 5.26/5.2 | 5.2 | 5.26/5.2 | 5.2 | 5.26/5.2 | 10.86 | 10.86 | 10.86 | 10.8/5.75/5.2 | 10.86 | 10.8/5.75/5.2 | 10.86 | 10.86 | 10.86 | 10.86 | 10.3 | 10.3
| Rated load Amps(RLA) | A | 11.8 | 10.6/11.8 | 11.8 | 10.6/11.8 | 11.8 | 10.6/11.8 | 11.8 | 10.6/11.8 | 21.4 | 21.4 | 21.4 | 21.1/12.7/11.8 | 21.4 | 21.1/12.7/11.8 | 21.4 | 21.4 | 21.4 | 21.4 | 20.7 | 20.7
| Locked rotor Amp(LRA) | A | 74 | 74/74 | 74 | 74/74 | 74 | 74/74 | 74 | 74/74 | 147 | 147 | 147 | 144/82.4/74 | 147 | 144/82.4/74 | 147 | 147 | 147 | 147 | 142 | 142
| Refrigerant oil | ml | 1656 | 1892/1656 | 1892 | 1892/1656 | 1892 | 1892/1656 | 1892 | 1892/1656 | 3300 | 3300 | 3300 | 3200/1893/1685 | 3300 | 3200/1893/1685 | 3300 | 3300 | 3300 | 3300 | 3300 | 3300
Refrigerant | Type |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A
| Refrigerant control |  | EXV | EXV | EXV | EXV | EXV | EXV | EXV | EXV | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary | EXV+ capillary
| Weight | kg | 3.5×2 | 3.5×2 | 3.5×2 | 3.5×2 | 3.5×2 | 3.5×2 | 3.5×2 | 3.5×2 | 7.0×2 | 7.0×2 | 7.0×2 | 7.0×2 | 7.0×2 | 7.0×2 | 7.0×4 | 7.0×4 | 7.0×6 | 7.0×6 | 15×4 | 15×4
Condenser (Air side) | Type |  | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil | Fin-coil
| Number of rows |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Fan motor model |  | YDK400-8-YA | YDK400-8-YA | YDK400-8-YA | YDK400-8-YA | YDK550-6E | YDK550-6E | YDK550-6E | YDK550-6E | YDK550-6D | YDK550-6D | YDK550-6D | YDK550-6E | YDK550-6E | YDK550-6E | YDK550-6D | YDK550-6E | YDK550-6D | YDK550-6E | YS700-6F-1/YS700-6F-2 | YDK550-6E
| Quantity of fan motor | Pieces | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 4 | 6 | 6 | 6/2 | 8
| Air flow | ×103m3/h | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 24 | 24 | 24 | 24 | 24 | 24 | 48 | 48 | 72 | 72 | 96 | 96
| Fan motor rated current | A | 3.1 | 3.1 | 3.1 | 3.1 | 4 | 4 | 4 | 4 | 4.0×2 | 4.0×2 | 4.0×2 | 4.0×2 | 4.0×2 | 4.0×2 | 4.0×4 | 4.0×4 | 4.0×6 | 4.0×6 | 1.8×8 | 3.7×8
| Fan motor power input | kW | 0.67 | 0.67 | 0.67 | 0.67 | 0.865 | 0.865 | 0.865 | 0.865 | 0.865×2 | 0.865×2 | 0.865×2 | 0.865×2 | 0.865×2 | 0.865×2 | 0.865×4 | 0.865×4 | 0.865×6 | 0.865×6 | 0.7×8 | 0.8×8
Evaporator (Water side) | Type |  | Double-pipe | Double-pipe | Double-pipe | Double-pipe | Double-pipe | Double-pipe | Double-pipe | Double-pipe | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube | Shell-tube
| Water pressure drop | kPa | 60 | 60 | 60 | 60 | / | / | 60 | 60 | 15 | 15 | 15 | 15 | 15 | 15 | 25 | 25 | 30 | 30 | 40 | 40
| Volume | L | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 42 | 42 | 42 | 42 | 42 | 42 | 64 | 64 | 90 | 90 | 131 | 131
| Water inlet/outlet pipeline inside normal diameter | mm | DN40 | DN40 | DN40 | DN40 | DN40 | DN40 | DN40 | DN40 | DN100 | DN100 | DN100 | DN100 | DN100 | DN100 | DN65 | DN65 | DN80 | DN80 | DN100 | DN100
| Water flow volume | m3/h | 4.4 | 4.4 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 9.4 | 10.3 | 11.2 | 11.2 | 11.2 | 11.2 | 22.4 | 22.4 | 31.8 | 31.8 | 43 | 43
| Max. Pressure | MPa | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Water pipe connection type |  | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint | Flexible joint
Dimension | Net(D×H×W) | mm | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 1514×1865×841 | 2000×1880×900 | 2000×1880×900 | 2000×1880×900 | 2000×1880×900 | 2000×1880×900 | 2000×1880×900 | 2000×2090×1685 | 2000×2090×1685 | 2850×2110×2000 | 2850×2110×2000 | 3800×2130×2000 | 3800×2130×2000
| Packing(D×H×W) | mm | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 1590×2065×995 | 2090×2055×985 | 2090×2055×985 | 2090×2055×985 | 2090×2055×985 | 2106×2090×998 | 2106×2090×998 | 2090×2240×1755 | 2090×2240×1755 | 2980×2260×2135 | 2980×2260×2135 | 3900×2200×2100 | 3900×2200×2100
Weight | Net weight | kg | 380 | 380 | 380 | 380 | 430 | 430 | 375 | 375 | 580 | 580 | 580 | 600 | 580 | 610 | 1150 | 1150 | 1730 | 1730 | 2450 | 2450
| Operation weight | kg | 420 | 420 | 420 | 420 | 450 | 450 | 400 | 400 | 650 | 650 | 650 | 670 | 650 | 680 | 1270 | 1270 | 2000 | 2000 | 2600 | 2600
Connection wiring | Power wire | mm2 | 10×4+10×1 | 10×4+10×1 | 10×4+10×1 | 10×4+10×1 | 10×4+6×1 | 10×4+6×1 | 10×4+6×1 | 10×4+6×1 | 16×4+6×1 | 16×4+10×1 | 16×4+10×1 | 25×4+16×1 | 25×4+16×1 | 25×4+16×1 | 35×3+16×2 | 35×3+16×2 | 75×3+35×2 | 75×3+35×2 | 185×4+70×1 | 150×4+70×1
| Signal wire | mm2 | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding | 0.75×3-core with shielding
Control type |  |  | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller
Noise level |  | dB(A) | 65 | 65 | 65 | 65 | 67 | 67 | 65 | 65 | 67 | 67 | 67 | 67 | 67 | 67 | 70 | 70 | 74 | 74 | 74 | 74
Operation water temp |  | ℃ | Cooling：5～17 Heating：45～50 | Cooling：5～17 Heating：45～50 | Cooling：5～17 Heating：45～50 | Cooling：5～17 Heating：45～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：5～17 Heating：45～50 | Cooling：5～17 Heating：45～50 | Cooling：5～17 Heating：45～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：5～17 Heating：45～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：5～17 Heating：45～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50 | Cooling：0～17(Less than 5℃ must add antifreeze) Heating：22～50
Ambient temp |  | ℃ | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～24 | Cooling：-10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：10～46 Heating：-10～21 | Cooling：-10～46 Heating：-10～21 | Cooling：10～52 Heating：-10～21 | Cooling：-10～46 Heating：-10～21
Note: Specifications are based on the following conditions:
• Cooling : chilled water inlet/outlet: 12℃ / 7℃, and outdoor ambient temp. of 35°C DB.
• Heating : warm water inlet/outlet: 40℃ / 45℃, and outdoor ambient temp. 7°CDB/6°CWB.
• Water side fouling factor: 0.086m2·℃/kW.