## 50HZ
Model |  |  | MGC-V5W/D2N1 | MGC-V7W/D2N1 | MGC-V10W/D2N1 | MGC-V12W/D2RN1 | MGC-V14W/D2RN1 | MGC-V16W/D2RN1
Power supply |  | V-Ph-Hz | 220-240, 1, 50 | 220-240, 1, 50 | 220-240, 1, 50 | 380-415, 3, 50 | 380-415, 3, 50 | 380-415, 3, 50
Cooling*(1) | Capacity | kW | 5 | 7 | 10.0(2.9~10.5) | 11.2(3.1~12.0) | 12.5(3.3~14) | 14.5(3.5~15.5)
| Input | kW | 1.55 | 2.25 | 2.95 | 3.38 | 3.9 | 4.53
Cooling*(2) | Capacity | kW | 6.57 | 7.88 | 10.9 | 14.5 | 15.17 | 16.7
| Input | kW | 1.27 | 1.84 | 2.49 | 2.8 | 3.13 | 3.73
Heating*(3) | Capacity | kW | 5.5 | 8 | 11.0(3.2~12.0) | 12.3(3.3~13.2) | 13.8(3.5~15.4) | 16.0(3.7~17.0)
| Input | kW | 1.7 | 2.5 | 3.14 | 3.72 | 4.25 | 4.85
Heating*(4) | Capacity | kW | 6.32 | 8.29 | 10.96 | 13.75 | 15.3 | 16.97
| Input | kW | 1.52 | 2.13 | 2.51 | 2.85 | 3.15 | 3.86
EER*（1） |  | kW/kW | 3.23 | 3.11 | 3.39 | 3.31 | 3.2 | 3.2
EER*（2） |  | kW/kW | 5.16 | 4.28 | 4.39 | 5.17 | 4.84 | 4.48
Max. input consumption |  | kW | 2.8 | 3 | 4.8 | 5.2 | 5.6 | 5.9
Max. input current |  | A | 14.6 | 15.6 | 25 | 8.9 | 9.6 | 10.1
Compressor | Model |  | SNB172FJGMC | SNB172FJGMC | ATQ420D1UMU | ATQ420D2UMU | ATQ420D2UMU | ATQ420D2UMU
| Type |  | ROTARY | ROTARY | ROTARY | ROTARY | ROTARY | ROTARY
| Brand |  | Mitsubishi Electric | Mitsubishi Electric | GMCC | GMCC | GMCC | GMCC
| Capacity | kW | 5.46 | 5.46 | 13.1 | 13 | 13 | 13
| Input | kW | 1.64 | 1.64 | 3.42 | 3.45 | 3.45 | 3.45
| Rated load current | A | 8.1 | 8.1 | 6.85 | 6.9 | 6.9 | 6.9
| Locked rotor Amp | A | 29.5 | 29.5 | 52 | 44 | 44 | 44
| Thermal protector |  | Inner | Inner | Inner | Inner | Inner | Inner
| Refrigerant oil | ml | FV50S,400 | FV50S,400 | VG74,1400 | VG74,1400 | VG74,1400 | VG74,1400
Outdoor fan motor | Model |  | WZDK170-38G-1 | WZDK170-38G-1 | WZDK100-38G | WZDK100-38G | WZDK100-38G | WZDK100-38G
| Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Brand |  | NIDEC SHIBAURA | NIDEC SHIBAURA | Panasonic | Panasonic | Panasonic | Panasonic
| Input | W | 170 | 170 | 100 | 100 | 100 | 100
| Speed | r/min | 820 | 820 | 800 | 800 | 800 | 800
Outdoor coil | Number of rows |  | 2 | 2 | 2 | 2 | 2 | 2
| Tube pitch(a)× row pitch(b) | mm | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05
| Fin spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Fin type |  | Hydrophilic aluminum foil | Hydrophilic aluminum foil | Hydrophilic aluminum foil | Hydrophilic aluminum foil | Hydrophilic aluminum foil | Hydrophilic aluminum foil
| Tube outside dia. and type | mm | φ7.94 | φ7.94 | φ7.94 | φ7.94 | φ7.94 | φ7.94
|  |  | Inner grooved copper tube | Inner grooved copper tube | Inner grooved copper tube | Inner grooved copper tube | Inner grooved copper tube | Inner grooved copper tube
| Coil length ×height | mm | 885×880 | 885×880 | 1276×870 | 1276×870 | 1276×870 | 1276×870
| Number of circuits |  | 6 | 6 | 7 | 7 | 7 | 7
Water pump | Type |  | RS15/6-3-WILO | RS15/6-3-WILO | RL25/8.5 | RL25/8.5 | RL25/8.5 | RL25/8.5
| Input (H/M/L) | W | 93/67/46 | 93/67/46 | 210/175/120 | 210/175/120 | 210/175/120 | 210/175/120
| Pumping head | m | 5.5 | 5.5 | 8 | 8 | 8 | 8
Outdoor air flow |  | m3/h | 5100 | 5100 | 7000 | 7000 | 7000 | 7000
Throttle |  |  | EXV+capillary | EXV+capillary | EXV | EXV | EXV | EXV
Outdoor noise level (sound pressure)*(3) |  | dB(A) | 58 | 58 | 59 | 59 | 60 | 60
Water flow |  | m3/h | 0.86 | 1.2 | 1.72 | 1.92 | 2.15 | 2.49
The plate heat-exchanger water pressure drop |  | kPa | 15 | 15 | 18 | 18 | 18 | 19
The Max. and Min. water inlet pressure |  | kPa | 500/150 | 500/150 | 500/150 | 500/150 | 500/150 | 500/150
Outdoor unit | Net dimension (W×H×D) | mm | 990×966×354 | 990×966×354 | 970×1327×400 | 970×1327×400 | 970×1327×400 | 970×1327×400
| Packing dimension (W×H×D) | mm | 1120×1100×435 | 1120×1100×435 | 1082×1456×435 | 1082×1456×435 | 1082×1456×435 | 1082×1456×435
| Net/ Gross weight | kg | 81/91 | 81/91 | 110/121 | 110/121 | 111/122 | 111/122
Refrigerant | Type |  | R410A | R410A | R410A | R410A | R410A | R410A
| Charged volume | kg | 2.5 | 2.5 | 2.8 | 2.8 | 2.9 | 3.2
Connection wiring | Power wire | mm2 | 3×2.5 | 3×2.5 | 3×4.0 | 5×3.0 | 5×3.0 | 5×3.0
| Signal wire | mm2 | 3×0.75 | 3×0.75 | 3×0.75 | 3×0.75 | 3×0.75 | 3×0.75
Pipe diameter | Water inlet/outlet | inch | 1’’ | 1’’ | 1-1/4“ | 1-1/4“ | 1-1/4“ | 1-1/4“
Control |  |  | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller | Wired controller
Ambient temperature |  | ℃ | Cooling: -5℃~46℃; Heating: -15-27℃ |  | Cooling: -5℃~46℃; Heating: -15-27℃ |  | Cooling: -5℃~46℃; Heating: -15-27℃
Water outlet temperature range |  | ℃ | Cooling: 4~20 ℃; Heating: 30~55 ℃ |  | Cooling: 4~20 ℃; Heating: 30~55 ℃ |  | Cooling: 4~20 ℃; Heating: 30~55 ℃
1. Cooling: (*1) chilled water inlet/outlet temperature: 12/7°C,outdoor ambient temperature 35°C DB.
(*2) chilled water inlet/outlet temperature: 23/18°C,outdoor ambient temperature 35°C DB.
2. Heating: (*3) warm water inlet/outlet temperature: 40/45°C,outdoor ambient temperature 7°C DB/6°C WB .
(*4) warm water inlet/outlet temperature: 30/35°C,outdoor ambient temperature 7°C DB/6°C WB .
3. It is tested 1m away in front of the unit in a semi-anechoic room(sound pressure).
4. The above data may be changed without notice for future improvement on quality and performance.