## 手册祥参8～22HP
Model |  |  | MV5-X252W/V2GN1 | MV5-X280W/V2GN1 | MV5-X335W/V2GN1 | MV5-X400W/V2GN1 | MV5-X450W/V2GN1 | MV5-X500W/V2GN1 | MV5-X560W/V2GN1 | MV5-X615W/V2GN1
HP |  |  | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22
|  |  | 220095103940 | 220095103930 | 220095103950 | 220095103960 | 220095103970 | 220095103980 | 220095103990 | 220095104000
Power source |  | V-Ph-Hz | 8: 380～415V 3N 50Hz/60Hz; 16: 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 25.2 | 28 | 33.5 | 40 | 45 | 50 | 56 | 61.5
|  | RT | 7.2 | 8 | 9.5 | 11.4 | 12.8 | 14.3 | 16 | 17.5714
|  | kBtu/h | 86 | 95.5 | 114.3 | 136.5 | 153.5 | 170.6 | 191.1 | 209.8
|  | kcal/h | 21672 | 24080 | 28810 | 34400 | 38700 | 43000 | 48160 | 52890
| Power input | kW | 5.79 | 7.02 | 8.71 | 10.81 | 12.83 | 14.47 | 16.67 | 18.77
| EER | kW/kW | 4.3523 | 3.9886 | 3.8462 | 3.7003 | 3.5074 | 3.46 | 3.3593 | 3.2765
Heating | Capacity | kW | 27 | 31.5 | 37.5 | 45 | 50 | 56 | 63 | 69
|  | RT | 7.7 | 8.9 | 10.7 | 12.8 | 14.2 | 16 | 18 | 19.7143
|  | kBtu/h | 92.1 | 107.5 | 128 | 153.5 | 170.6 | 191.1 | 214.9 | 235.4
|  | kcal/h | 23220 | 27090 | 32250 | 38700 | 43000 | 48160 | 54180 | 59340
| Power input | kW | 5.79 | 7.19 | 8.82 | 10.98 | 12.47 | 14.15 | 15.98 | 17.86
| COP | kW/kW | 4.6632 | 4.3811 | 4.2517 | 4.0984 | 4.0096 | 3.9576 | 3.9424 | 3.8634
DC inverter compressor | Model |  | E655DHD-65D2YG | E655DHD-65D2YG | E705DHD-72D2YG | E405DHD-42D2YG | E405DHD-42D2YG | E405DHD-36D2YG E705DHD-72D2YG | E705DHD-72D2YG | E705DHD-72D2YG
| Quantities |  | 1 | 1 | 1 | 2 | 2 | 1+1 | 2 | 2
| Type |  | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi | Hitachi | Hitachi | Hitachi | Hitachi | Hitachi
| Capacity | kW | 21.06 | 21.06 | 23.25 | 13.8×2 | 13.8×2 | 11.8+23.25 | 23.25×2 | 23.25×2
|  | kBtu/h | 71.9 | 71.9 | 79.3 | 47.1×2 | 47.1×2 | 40.3+79.3 | 79.3×2 | 79.3×2
| Crankcase heater | W | 27.6×2 | 27.6×2 | 27.6×2 | 27.6×4 | 27.6×4 | 27.6×4 | 27.6×4 | 27.6×4
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D | FVC68D | FVC68D | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132(500) | 0.132(500) | 0.132(500) | 0.132(500)×2 | 0.132(500)×2 | 0.132(500)×2 | 0.132(500)×2 | 0.132(500)×2
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor | DC motor | DC motor | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2
Insulation class | bar: 8 to 22
| Safe class |  | IP23 | IP23 | IP23 | IP23 | IP23 | IP23 | IP23 | IP23
| Input | W | 580 | 580 | 580 | 360+290 | 360+290 | 520+440 | 550+430 | 550+430
| Output | W | 465 | 465 | 465 | 290+230 | 290+230 | 420+350 | 440+350 | 440+350
Outdoor fan | Material |  | Plastic | Plastic | Plastic | Plastic | Plastic | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial | Axial | Axial | Axial | Axial | Axial
| Fan Quantities |  | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2
| External static pressure | in. W.G.(Pa) | 8: 0～0.08(0~20) (default); 16: 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 8: 0.08~0.16(20~40) (customized); 16: 0.08~0.16(20~40) (customized)
Outdoor coil | Number of rows |  | 2 | 2 | 3 | 2 | 2 | 2 | 3 | 3
| Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | 8: Hydrophilic aluminum; 16: Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved | Inner-grooved | Inner-grooved | Inner-grooved | Inner-grooved | Inner-grooved
| Coil length × height | in.(mm) | 77-9/16×48-1/2 (1970×1232) | 77-9/16×48-1/2 (1970×1232) | 77-9/16×48-1/2 (1970×1232) | 91-3/8×48-1/2 （2320×1232） | 91-3/8×48-1/2 （2320×1232） | 89-3/8×48-1/2 （2270×1232） | 89-3/8×48-1/2 （2270×1232） | 89-3/8×48-1/2 （2270×1232）
| Number of circuits |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
Outdoor air flow |  | m3/h | 10800 | 10800 | 10800 | 14000 | 14000 | 15500 | 15500 | 15500
|  | CFM | 6360 | 6360 | 6360 | 8240 | 8240 | 9120 | 9120 | 9120
Sound pressure level |  | dB(A) | 43～58 | 43～59 | 43～60 | 43～62 | 43～62 | 43～63 | 43～63 | 43～63
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130 | 50-130 | 50-130 | 50-130 | 50-130 | 50-130
| Max. quantity |  | 13 | 16 | 19 | 23 | 26 | 29 | 33 | 36
Outdoor unit | Dimension(W×H×D) | inch | 13: 39×64-3/8×31-1/8; 23: 52-3/4×64-3/8×31-1/8; 26: 52-3/4×64-3/8×31-1/8
|  | mm | 13: 990×1635×790; 23: 1340×1635×790; 26: 1340×1635×790
| Packing(W×H×D) | inch | 13: 41-1/2×71-1/16×33-5/8; 23: 55-3/8×71-1/16×33-5/8; 26: 55-3/8×71-1/16×33-5/8
|  | mm | 13: 1055×1805×855; 23: 1405×1805×855; 26: 1405×1805×855
| Net weight | lbs.(kg) | 483(219) | 483(219) | 523(237) | 655(297) | 655(297) | 673(305) | 750(340) | 750(340)
| Gross weight | lbs.(kg) | 516(234) | 516(234) | 556(252) | 695(315) | 695(315) | 712(323) | 790(358) | 790(358)
Refrigerant | Type |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 20(9) | 20(9) | 24(11) | 29(13) | 29(13) | 29(13) | 35(16) | 35(16)
Throttle type |  |  | EXV | EXV | EXV | EXV | EXV | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6 | 4.4/2.6 | 4.4/2.6 | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380 | 640/380 | 640/380 | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ3/8(Φ9.53) | Φ3/8(Φ9.53) | Φ1/2(Φ12.7) | Φ1/2(Φ12.7) | Φ1/2(Φ12.7) | Ф5/8(Ф15.9) | Ф5/8(Ф15.9) | Ф5/8(Ф15.9)
| Gas pipe | in.(mm) | Φ7/8(Φ22.2) | Φ7/8(Φ22.2) | Φ1(Φ25.4) | Φ1(Φ25.4) | Ф1-1/8(Ф28.6) | Ф1-1/8(Ф28.6) | Ф1-1/8(Ф28.6) | Ф1-1/8(Ф28.6)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 13: 23~118.4(-5~48); 26: 23~118.4(-5~48)
| Heating | °F(°C) | 13: -4~75.2(-20~24); 26: -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 24～28HP
|  |  | 24 | 26 | 28
Model | Combination Unit |  | MV5-X670W/V2GN1 | MV5-X730W/V2GN1 | MV5-X780W/V2GN1
| Independent Unit |  | MV5-X335W/V2GN1 | MV5-X280W/V2GN1 | MV5-X280W/V2GN1
|  |  | MV5-X335W/V2GN1 | MV5-X450W/V2GN1 | MV5-X500W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 67 | 73 | 78
|  | RT | 19 | 20.8 | 22.3
|  | kBtu/h | 228.6 | 249 | 266.1
|  | kcal/h | 57620 | 62780 | 67080
| Power input | kW | 17.42 | 19.85 | 21.49
| EER | kW/kW | 3.8462 | 3.6776 | 3.6296
Heating | Capacity | kW | 75 | 81.5 | 87.5
|  | RT | 21.4 | 23.1 | 24.9
|  | kBtu/h | 256 | 278.1 | 298.6
|  | kcal/h | 64500 | 70090 | 75250
| Power input | kW | 17.64 | 19.66 | 21.34
| COP | kW/kW | 4.2517 | 4.1455 | 4.1003
DC inverter compressor | Model |  | E705DHD-72D2YG×2 | E655DHD-65D2YG+ E405DHD-42D2YG×2 | E655DHD-65D2YG+ E405DHD-36D2YG+ E705DHD-72D2YG
| Quantities |  | 2 | 3 | 3
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 46.5 | 21.06+(13.8×2) | 21.06+(11.8+23.25)
|  | kBtu/h | 158.6 | 71.9+(47.1×2) | 71.9+(40.3+79.3)
| Crankcase heater | W | 27.6×4 | 27.6×6 | 27.6×6
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×2(500×2) | 0.132×3(500×3) | 0.132×3(500×3)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 2 | 3 | 3
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+580 | 580+(360+290) | 580+(520+440)
| Output | W | 465×2 | 465+(290+230) | 465+(420+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 2 | 3 | 3
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 21600 | 24800 | 26300
|  | CFM | 12720 | 14600 | 15480
Sound pressure level |  | dB(A) | 64 | 65 | 65
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 39 | 43 | 46
Outdoor unit | Dimension(W×H×D) | inch | (39×64-3/8×31-1/8)×2 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8
|  | mm | (990×1635×790)×2 | 990×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790
| Packing(W×H×D) | inch | (41-1/2×71-1/16×33-5/8)×2 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8
|  | mm | (1055×1805×855)×2 | 1055×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855
| Net weight | lbs.(kg) | 523(237)×2 | 483+655(219+297) | 483+673(219+305)
| Gross weight | lbs.(kg) | 556(252)×2 | 516+695(234+315) | 516+712(234+323)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 24×2(11×2) | 20+29(9+13) | 20+29(9+13)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Ф5/8(Ф15.9) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1)
| Gas pipe | in.(mm) | Ф1-1/8(Ф28.6) | Φ1-1/4(Φ31.8) | Φ1-1/4(Φ31.8)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 30～34HP
|  |  | 30 | 32 | 34
Model | Combination Unit |  | MV5-X840W/V2GN1 | MV5-X895W/V2GN1 | MV5-X950W/V2GN1
| Independent Unit |  | MV5-X280W/V2GN1 | MV5-X280W/V2GN1 | MV5-X335W/V2GN1
|  |  | MV5-X560W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 84 | 89.5 | 95
|  | RT | 24 | 25.5714 | 27.0714
|  | kBtu/h | 286.6 | 305.3 | 324.1
|  | kcal/h | 72240 | 76970 | 81700
| Power input | kW | 23.69 | 25.79 | 27.48
| EER | kW/kW | 3.5458 | 3.4703 | 3.4571
Heating | Capacity | kW | 94.5 | 100.5 | 106.5
|  | RT | 26.9 | 28.6143 | 30.4143
|  | kBtu/h | 322.4 | 342.9 | 363.4
|  | kcal/h | 81270 | 86430 | 91590
| Power input | kW | 23.17 | 25.05 | 26.68
| COP | kW/kW | 4.0785 | 4.012 | 3.9918
DC inverter compressor | Model |  | E655DHD-65D2YG+ E705DHD-72D2YG×2 | E655DHD-65D2YG+ E705DHD-72D2YG×2 | E705DHD-72D2YG×3
| Quantities |  | 3 | 3 | 3
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 21.06+(23.25×2) | 21.06+(23.25×2) | 23.25+(23.25×2)
|  | kBtu/h | 71.9+(79.3×2) | 71.9+(79.3×2) | 79.3+(79.3×2)
| Crankcase heater | W | 27.6×6 | 27.6×6 | 27.6×6
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×3(500×3) | 0.132×3(500×3) | 0.132×3(500×3)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 3 | 3 | 3
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+(550+430) | 580+(550+430) | 580+(550+430)
| Output | W | 465+(440+350) | 465+(440+350) | 465+(440+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 3 | 3 | 3
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 26300 | 26300 | 26300
|  | CFM | 15480 | 15480 | 15480
Sound pressure level |  | dB(A) | 65 | 65 | 65
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 50 | 53 | 56
Outdoor unit | Dimension(W×H×D) | inch | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8
|  | mm | 990×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790
| Packing(W×H×D) | inch | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8
|  | mm | 1055×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855
| Net weight | lbs.(kg) | 483+750(219+340) | 483+750(219+340) | 523+750(237+340)
| Gross weight | lbs.(kg) | 516+790(234+358) | 516+790(234+358) | 556+790(252+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 20+35(9+16) | 20+35(9+16) | 24+35(11+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1)
| Gas pipe | in.(mm) | Φ1-1/4(Φ31.8) | Φ1-1/4(Φ31.8) | Φ1-1/4(Φ31.8)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)

## 36~40HP
|  |  | 36 | 38 | 40
Model | Combination Unit |  | MV5-X1000W/V2GN1 | MV5-X1065W/V2GN1 | MV5-X1115W/V2GN1
| Independent Unit |  | MV5-X500W/V2GN1 | MV5-X450W/V2GN1 | MV5-X500W/V2GN1
|  |  | MV5-X500W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 100 | 106.5 | 111.5
|  | RT | 28.6 | 30.3714 | 31.8714
|  | kBtu/h | 341.2 | 363.3 | 380.4
|  | kcal/h | 86000 | 91590 | 95890
| Power input | kW | 28.94 | 31.6 | 33.24
| EER | kW/kW | 3.4554 | 3.3703 | 3.3544
Heating | Capacity | kW | 112 | 119 | 125
|  | RT | 32 | 33.9143 | 35.7143
|  | kBtu/h | 382.2 | 406 | 426.5
|  | kcal/h | 96320 | 102340 | 107500
| Power input | kW | 28.3 | 30.33 | 32.01
| COP | kW/kW | 3.9576 | 3.9235 | 3.905
DC inverter compressor | Model |  | E405DHD-36D2YG×2+ E705DHD-72D2YG×2 | E405DHD-42D2YG×2+ E705DHD-72D2YG×2 | E405DHD-36D2YG+ E705DHD-72D2YG×3
| Quantities |  | 4 | 4 | 4
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | (11.8+23.25)×2 | (13.8×2)+(23.25×2) | (11.8+23.25)+(23.25×2)
|  | kBtu/h | (40.3+79.3)×2 | (47.1×2)+(79.3×2) | (40.3+79.3)+(79.3×2)
| Crankcase heater | W | 27.6×8 | 27.6×8 | 27.6×8
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×4(500×4) | 0.132×4(500×4) | 0.132×4(500×4)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 4 | 4 | 4
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | (520+440)×2 | (360+290)+(550+430) | (520+440)+(550+430)
| Output | W | (420+350)×2 | (290+230)+(440+350) | (420+350)+(440+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 4 | 4 | 4
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 31000 | 29500 | 31000
|  | CFM | 18240 | 17360 | 18240
Sound pressure level |  | dB(A) | 66 | 66 | 66
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 59 | 63 | 64
Outdoor unit | Dimension(W×H×D) | inch | (52-3/4×64-3/8×31-1/8)×2 | 52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8
|  | mm | (1340×1635×790)×2 | 1340×1635×790 +1340×1635×790 | 1340×1635×790 +1340×1635×790
| Packing(W×H×D) | inch | (55-3/8×71-1/16×33-5/8)×2 | 55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8
|  | mm | (1405×1805×855)×2 | 1405×1805×855 +1405×1805×855 | 1405×1805×855 +1405×1805×855
| Net weight | lbs.(kg) | 673×2(305×2) | 655+750(297+340) | 673+750(305+340)
| Gross weight | lbs.(kg) | 712×2(323×2) | 695+790(315+358) | 712+790(323+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 29×2(13×2) | 29+35(13+16) | 29+35(13+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1)
| Gas pipe | in.(mm) | Φ1-1/2(Φ38.1) | Φ1-1/2(Φ38.1) | Φ1-1/2(Φ38.1)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)

## 42~46HP
|  |  | 42 | 44 | 46
Model | Combination Unit |  | MV5-X1175W/V2GN1 | MV5-X1230W/V2GN1 | MV5-X1285W/V2GN1
| Independent Unit |  | MV5-X560W/V2GN1 | MV5-X615W/V2GN1 | MV5-X335W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X335W/V2GN1
|  |  | - | - | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 117.5 | 123 | 128.5
|  | RT | 33.5714 | 35.1429 | 36.5714
|  | kBtu/h | 400.9 | 419.6 | 438.4
|  | kcal/h | 101050 | 105780 | 110510
| Power input | kW | 35.44 | 37.54 | 36.19
| EER | kW/kW | 3.3155 | 3.2765 | 3.5507
Heating | Capacity | kW | 132 | 138 | 144
|  | RT | 37.7143 | 39.4286 | 41.1143
|  | kBtu/h | 450.3 | 470.8 | 491.4
|  | kcal/h | 113520 | 118680 | 123840
| Power input | kW | 33.84 | 35.72 | 35.5
| COP | kW/kW | 3.9007 | 3.8634 | 4.0563
DC inverter compressor | Model |  | E705DHD-72D2YG×4 | E705DHD-72D2YG×4 | E705DHD-72D2YG×4
| Quantities |  | 4 | 4 | 4
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | (23.25×2)+(23.25×2) | (23.25×2)×2 | 23.25×2+23.25×2
|  | kBtu/h | (79.3×2)+(79.3×2) | (79.3×2)×2 | 79.3×2+79.3×2
| Crankcase heater | W | 27.6×8 | 27.6×8 | 27.6×8
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×4(500×4) | 0.132×4(500×4) | 0.132×4(500×4)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 4 | 4 | 4
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | (550+430)+(550+430) | (550+430)×2 | 580×2+(550+430)
| Output | W | (440+350)+(440+350) | (440+350)×2 | 465×2+(440+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 4 | 4 | 4
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 31000 | 31000 | 37100
|  | CFM | 18240 | 18240 | 21840
Sound pressure level |  | dB(A) | 66 | 66 | 66
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | (52-3/4×64-3/8×31-1/8)×2 | (39×64-3/8×31-1/8)×2 +52-3/4×64-3/8×31-1/8
|  | mm | 1340×1635×790 +1340×1635×790 | (1340×1635×790)×2 | (990×1635×790)×2 +1340×1635×790
| Packing(W×H×D) | inch | 55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | (55-3/8×71-1/16×33-5/8)×2 | (41-1/2×71-1/16×33-5/8)×2 +55-3/8×71-1/16×33-5/8
|  | mm | 1405×1805×855 +1405×1805×855 | (1405×1805×855)×2 | (1055×1805×855)×2 +1405×1805×855
| Net weight | lbs.(kg) | 750+750(340+340) | 750×2(340×2) | 523×2+750(237×2+340)
| Gross weight | lbs.(kg) | 790+790(358+358) | 790×2(358×2) | 556×2+790(252×2+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 35+35(16+16) | 35×2(16×2) | 24×2+35(11×2+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1)
| Gas pipe | in.(mm) | Φ1-1/2(Φ38.1) | Φ1-1/2(Φ38.1) | Φ1-1/2(Φ38.1)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)

## 48~52HP
|  |  | 48 | 50 | 52
Model | Combination Unit |  | MV5-X1345W/V2GN1 | MV5-X1395W/V2GN1 | MV5-X1455W/V2GN1
| Independent Unit |  | MV5-X280W/V2GN1 | MV5-X280W/V2GN1 | MV5-X280W/V2GN1
|  |  | MV5-X450W/V2GN1 | MV5-X500W/V2GN1 | MV5-X560W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 134.5 | 139.5 | 145.5
|  | RT | 38.3714 | 39.8714 | 41.5714
|  | kBtu/h | 458.8 | 475.9 | 496.4
|  | kcal/h | 115670 | 119970 | 125130
| Power input | kW | 38.62 | 40.26 | 42.46
| EER | kW/kW | 3.4827 | 3.465 | 3.4268
Heating | Capacity | kW | 150.5 | 156.5 | 163.5
|  | RT | 42.8143 | 44.6143 | 46.6143
|  | kBtu/h | 513.5 | 534 | 557.8
|  | kcal/h | 129430 | 134590 | 140610
| Power input | kW | 37.52 | 39.2 | 41.03
| COP | kW/kW | 4.0112 | 3.9923 | 3.9849
DC inverter compressor | Model |  | E655DHD-65D2YG+ E405DHD-42D2YG×2+ E705DHD-72D2YG×2 | E655DHD-65D2YG+ E405DHD-36D2YG+ E705DHD-72D2YG×3 | E655DHD-65D2YG+ E705DHD-72D2YG×4
| Quantities |  | 5 | 5 | 5
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 21.06+(13.8×2) +(23.25×2) | 21.06+(11.8+23.25) +(23.25×2) | 21.06+(23.25×2) +(23.25×2)
|  | kBtu/h | 71.9+(47.1×2) +(79.3×2) | 71.9+(40.3+79.3) +(79.3×2) | 71.9+(79.3×2) +(79.3×2)
| Crankcase heater | W | 27.6×10 | 27.6×10 | 27.6×10
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×5(500×5) | 0.132×5(500×5) | 0.132×5(500×5)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 5 | 5 | 5
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+(360+290) +(550+430) | 580+(520+440) +(550+430) | 580+(550+430) +(550+430)
| Output | W | 465+(290+230) +(440+350) | 465+(420+350) +(440+350) | 465+(440+350) +(440+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 5 | 5 | 5
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 40300 | 41800 | 41800
|  | CFM | 23720 | 24600 | 24600
Sound pressure level |  | dB(A) | 67 | 67 | 67
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8
|  | mm | 990×1635×790 +1340×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790 +1340×1635×790
| Packing(W×H×D) | inch | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8
|  | mm | 1055×1805×855 +1405×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855 +1405×1805×855
| Net weight | lbs.(kg) | 483+655+750 (219+297+340) | 483+673+750 (219+305+340) | 483+750+750 (219+340+340)
| Gross weight | lbs.(kg) | 516+695+790 (234+315+358) | 516+712+790 (234+323+358) | 516+790+790 (234+358+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 20+29+35(9+13+16) | 20+29+35(9+13+16) | 20+35+35(9+16+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ3/4(Φ19.1) | Φ3/4(Φ19.1) | Φ7/8(Φ22.2)
| Gas pipe | in.(mm) | Φ1-1/2(Φ38.1) | Φ1-1/2(Φ38.1) | Φ1-5/8(Φ41.2)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 54~58HP
|  |  | 54 | 56 | 58
Model | Combination Unit |  | MV5-X1510W/V2GN1 | MV5-X1565W/V2GN1 | MV5-X1615W/V2GN1
| Independent Unit |  | MV5-X280W/V2GN1 | MV5-X335W/V2GN1 | MV5-X500W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X500W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 151 | 156.5 | 161.5
|  | RT | 43.1429 | 44.6429 | 46.1714
|  | kBtu/h | 515.1 | 533.9 | 551
|  | kcal/h | 129860 | 134590 | 138890
| Power input | kW | 44.56 | 46.25 | 47.71
| EER | kW/kW | 3.3887 | 3.3838 | 3.385
Heating | Capacity | kW | 169.5 | 175.5 | 181
|  | RT | 48.3286 | 50.1286 | 51.7143
|  | kBtu/h | 578.3 | 598.8 | 617.6
|  | kcal/h | 145770 | 150930 | 155660
| Power input | kW | 42.91 | 44.54 | 46.16
| COP | kW/kW | 3.9501 | 3.9403 | 3.9211
DC inverter compressor | Model |  | E655DHD-65D2YG+ E705DHD-72D2YG×4 | E705DHD-72D2YG×5 | E405DHD-36D2YG×2+ E705DHD-72D2YG×4
| Quantities |  | 5 | 5 | 6
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 21.06+(23.25×2)×2 | 23.25+(23.25×2)×2 | (11.8+23.25)×2+23.25×2
|  | kBtu/h | 71.9+(79.3×2)×2 | 79.3+(79.3×2)×2 | (40.3+79.3)×2+79.3×2
| Crankcase heater | W | 27.6×10 | 27.6×10 | 27.6×12
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×5(500×5) | 0.132×5(500×5) | 0.132×6(500×6)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 5 | 5 | 6
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+(550+430)×2 | 580+(550+430)×2 | (520+440)×2+(550+430)
| Output | W | 465+(440+350)×2 | 465+(440+350)×2 | (420+350)×2+(440+350)
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 5 | 5 | 6
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 41800 | 41800 | 46500
|  | CFM | 24600 | 24600 | 27360
Sound pressure level |  | dB(A) | 67 | 67 | 68
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 39×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×2 | 39×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×2 | (52-3/4×64-3/8×31-1/8)×2 +52-3/4×64-3/8×31-1/8
|  | mm | 990×1635×790+ (1340×1635×790)×2 | 990×1635×790+ (1340×1635×790)×2 | (1340×1635×790)×2 +1340×1635×790
| Packing(W×H×D) | inch | 41-1/2×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×2 | 41-1/2×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×2 | (55-3/8×71-1/16×33-5/8)×2 +55-3/8×71-1/16×33-5/8
|  | mm | 1055×1805×855+ (1405×1805×855)×2 | 1055×1805×855+ (1405×1805×855)×2 | (1405×1805×855)×2 +1405×1805×855
| Net weight | lbs.(kg) | 483+750×2(219+340×2) | 523+750×2(237+340×2) | 673×2+750(305×2+340)
| Gross weight | lbs.(kg) | 516+790×2(234+358×2) | 556+790×2(252+358×2) | 712×2+323(323×2+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 20+35×2(9+16×2) | 24+35×2(11+16×2) | 29×2+35(13×2+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ7/8(Φ22.2) | Φ7/8(Φ22.2) | Φ7/8(Φ22.2)
| Gas pipe | in.(mm) | Φ1-5/8(Φ41.2) | Φ1-5/8(Φ41.2) | Φ1-5/8(Φ41.2)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 60~64HP
|  |  | 60 | 62 | 64
Model | Combination Unit |  | MV5-X1680W/V2GN1 | MV5-X1730W/V2GN1 | MV5-X1790W/V2GN1
| Independent Unit |  | MV5-X450W/V2GN1 | MV5-X500W/V2GN1 | MV5-X560W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 168 | 173 | 179
|  | RT | 47.9429 | 49.4429 | 51.1429
|  | kBtu/h | 573.1 | 590.2 | 610.7
|  | kcal/h | 144480 | 148780 | 153940
| Power input | kW | 50.37 | 52.01 | 54.21
| EER | kW/kW | 3.3353 | 3.3263 | 3.302
Heating | Capacity | kW | 188 | 194 | 201
|  | RT | 53.6286 | 55.4286 | 57.4286
|  | kBtu/h | 641.4 | 661.9 | 685.7
|  | kcal/h | 161680 | 166840 | 172860
| Power input | kW | 48.19 | 49.87 | 51.7
| COP | kW/kW | 3.9012 | 3.8901 | 3.8878
DC inverter compressor | Model |  | E405DHD-42D2YG×2+ E705DHD-72D2YG×4 | E405DHD-36D2YG+ E705DHD-72D2YG×6 | E705DHD-72D2YG×6
| Quantities |  | 6 | 6 | 6
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 13.8×2+(23.25×2)×2 | (11.8+23.25)+(23.25×2)×2 | 23.25×2+(23.25×2)×2
|  | kBtu/h | 47.1×2+(79.3×2)×2 | (40.3+79.3)+(79.3×2)×2 | 79.3×2+(79.3×2)×2
| Crankcase heater | W | 27.6×12 | 27.6×12 | 27.6×12
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×6(500×6) | 0.132×6(500×6) | 0.132×6(500×6)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 6 | 6 | 6
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | (360+290)+(550+430)×2 | (520+440)+(550+430)×2 | (550+430)+(550+430)×2
| Output | W | (290+230)+(440+350)×2 | (420+350)+(440+350)×2 | (440+350)+(440+350)×2
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 6 | 6 | 6
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 45000 | 46500 | 46500
|  | CFM | 26480 | 27360 | 27360
Sound pressure level |  | dB(A) | 68 | 68 | 68
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×2 | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×2 | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×2
|  | mm | 1340×1635×790+ (1340×1635×790)×2 | 1340×1635×790+ (1340×1635×790)×2 | 1340×1635×790+ (1340×1635×790)×2
| Packing(W×H×D) | inch | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×2 | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×2 | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×2
|  | mm | 1405×1805×855+ (1405×1805×855)×2 | 1405×1805×855+ (1405×1805×855)×2 | 1405×1805×855+ (1405×1805×855)×2
| Net weight | lbs.(kg) | 655+750×2(297+340×2) | 673+750×2(305+340×2) | 750+750×2(340+340×2)
| Gross weight | lbs.(kg) | 695+790×2(315+358×2) | 712+790×2(323+358×2) | 790+790×2(358+358×2)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 29+35×2(13+16×2) | 29+35×2(13+16×2) | 35+35×2(16+16×2)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ7/8(Φ22.2) | Φ7/8(Φ22.2) | Φ7/8(Φ22.2)
| Gas pipe | in.(mm) | Φ1-5/8(Φ41.2) | Φ1-5/8(Φ41.2) | Φ1-5/8(Φ41.2)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 66~70HP
|  |  | 66 | 68 | 70
Model | Combination Unit |  | MV5-X1845W/V2GN1 | MV5-X1900W/V2GN1 | MV5-X1960W/V2GN1
| Independent Unit |  | MV5-X615W/V2GN1 | MV5-X335W/V2GN1 | MV5-X280W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X335W/V2GN1 | MV5-X450W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | - | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 184.5 | 190 | 196
|  | RT | 52.7143 | 54.1429 | 55.9429
|  | kBtu/h | 629.4 | 648.2 | 668.6
|  | kcal/h | 158670 | 163400 | 168560
| Power input | kW | 56.31 | 54.96 | 57.39
| EER | kW/kW | 3.2765 | 3.4571 | 3.4152
Heating | Capacity | kW | 207 | 213 | 219.5
|  | RT | 59.1429 | 60.8286 | 62.5286
|  | kBtu/h | 706.2 | 726.8 | 748.9
|  | kcal/h | 178020 | 183180 | 188770
| Power input | kW | 53.58 | 53.36 | 55.38
| COP | kW/kW | 3.8634 | 3.9918 | 3.9635
DC inverter compressor | Model |  | E705DHD-72D2YG×6 | E705DHD-72D2YG×6 | E655DHD-65D2YG+ E405DHD-42D2YG×2+ E705DHD-72D2YG×4
| Quantities |  | 6 | 6 | 7
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | (23.25×2)×3 | 23.25×2+(23.25×2)×2 | 21.06+13.8×2+23.25×2
|  | kBtu/h | (79.3×2)×3 | 79.3×2+(79.3×2)×2 | 71.9+47.1×2+79.3×2
| Crankcase heater | W | 27.6×12 | 27.6×12 | 27.6×14
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×6(500×6) | 0.132×6(500×6) | 0.132×7(500×7)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 6 | 6 | 7
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | (550+430)×3 | 580×2+(550+430)×2 | 580+(360+290)+(550+430)×2
| Output | W | (440+350)×3 | 465×2+(440+350)×2 | 465+(290+230)+(440+350)×2
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 6 | 6 | 7
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 46500 | 52600 | 55800
|  | CFM | 27360 | 30960 | 32840
Sound pressure level |  | dB(A) | 68 | 68 | 69
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | (52-3/4×64-3/8×31-1/8)×3 | (39×64-3/8×31-1/8)×2+ (52-3/4×64-3/8×31-1/8)×2 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8
|  | mm | (1340×1635×790)×3 | (990×1635×790)×2+ (1340×1635×790)×2 | 990×1635×790 +1340×1635×790 +1340×1635×790
| Packing(W×H×D) | inch | (55-3/8×71-1/16×33-5/8)×3 | (41-1/2×71-1/16×33-5/8)×2+ (55-3/8×71-1/16×33-5/8)×2 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8
|  | mm | (1405×1805×855)×3 | (1055×1805×855)×2+ (1405×1805×855)×2 | 1055×1805×855 +1405×1805×855 +1405×1805×855
| Net weight | lbs.(kg) | 750×3(340×3) | 523×2+750×2(237×2+340×2) | 483+655+750(219+297+340)
| Gross weight | lbs.(kg) | 790×3(358×3) | 556×2+790×2(252×2+358×2) | 516+695+790(234+315+358)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 35×3(16×3) | 24×2+35×2(11×2+16×2) | 20+29+35(9+13+16)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ7/8(Φ22.2) | Φ1(Φ25.4) | Φ1(Φ25.4)
| Gas pipe | in.(mm) | Φ1-5/8(Φ41.2) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 72~76HP
|  |  | 72 | 74 | 76
Model | Combination Unit |  | MV5-X2010W/V2GN1 | MV5-X2070W/V2GN1 | MV5-X2125W/V2GN1
| Independent Unit |  | MV5-X280W/V2GN1 | MV5-X280W/V2GN1 | MV5-X280W/V2GN1
|  |  | MV5-X500W/V2GN1 | MV5-X560W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 201 | 207 | 212.5
|  | RT | 57.4429 | 59.1429 | 60.7143
|  | kBtu/h | 685.7 | 706.2 | 724.9
|  | kcal/h | 172860 | 178020 | 182750
| Power input | kW | 59.03 | 61.23 | 63.33
| EER | kW/kW | 3.405 | 3.3807 | 3.3554
Heating | Capacity | kW | 225.5 | 232.5 | 238.5
|  | RT | 64.3286 | 66.3286 | 68.0429
|  | kBtu/h | 769.4 | 793.2 | 813.7
|  | kcal/h | 193930 | 199950 | 205110
| Power input | kW | 57.06 | 58.89 | 60.77
| COP | kW/kW | 3.952 | 3.948 | 3.9246
DC inverter compressor | Model |  | E655DHD-65D2YG+ E405DHD-36D2YG+ E705DHD-72D2YG×5 | E655DHD-65D2YG+ E705DHD-72D2YG×6 | E655DHD-65D2YG+ E705DHD-72D2YG×6
| Quantities |  | 7 | 7 | 7
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 21.06+(11.8+23.25)+23.25×2 | 21.06+23.25×2+23.25×2 | 21.06+(23.25×2)×3
|  | kBtu/h | 71.9+(40.3+79.3)+79.3×2 | 71.9+79.3×2+79.3×2 | 71.9+(79.3×2)×3
| Crankcase heater | W | 27.6×14 | 27.6×14 | 27.6×14
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×7(500×7) | 0.132×7(500×7) | 0.132×7(500×7)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 7 | 7 | 7
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+(520+440)+(550+430)×2 | 580+(550+430)+(550+430)×2 | 580+(550+430)×3
| Output | W | 465+(420+350)+(440+350)×2 | 465+(440+350)+(440+350)×2 | 465+(440+350)×3
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 7 | 7 | 7
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 57300 | 57300 | 57300
|  | CFM | 33720 | 33720 | 33720
Sound pressure level |  | dB(A) | 69 | 69 | 69
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 +52-3/4×64-3/8×31-1/8 | 39×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×3
|  | mm | 990×1635×790 +1340×1635×790 +1340×1635×790 | 990×1635×790 +1340×1635×790 +1340×1635×790 | 990×1635×790+ (1340×1635×790)×3
| Packing(W×H×D) | inch | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 +55-3/8×71-1/16×33-5/8 | 41-1/2×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×3
|  | mm | 1055×1805×855 +1405×1805×855 +1405×1805×855 | 1055×1805×855 +1405×1805×855 +1405×1805×855 | 1055×1805×855+ (1405×1805×855)×3
| Net weight | lbs.(kg) | 483+673+750(219+305+340) | 483+750+750(219+340+340) | 483+750×3(219+340×3)
| Gross weight | lbs.(kg) | 516+712+790(234+323+358) | 516+790+790(234+358+358) | 516+790×3(234+358×3)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 20+29+35(9+13+16) | 20+35+35(9+16+16) | 20+35×3(9+16×3)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ1(Φ25.4) | Φ1(Φ25.4) | Φ1(Φ25.4)
| Gas pipe | in.(mm) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 78~82HP
|  |  | 78 | 80 | 82
Model | Combination Unit |  | MV5-X2180W/V2GN1 | MV5-X2230W/V2GN1 | MV5-X2295W/V2GN1
| Independent Unit |  | MV5-X335W/V2GN1 | MV5-X500W/V2GN1 | MV5-X450W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X500W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 218 | 223 | 229.5
|  | RT | 62.2143 | 63.7429 | 65.5143
|  | kBtu/h | 743.7 | 760.8 | 782.9
|  | kcal/h | 187480 | 191780 | 197370
| Power input | kW | 65.02 | 66.48 | 69.14
| EER | kW/kW | 3.3528 | 3.3544 | 3.3194
Heating | Capacity | kW | 244.5 | 250 | 257
|  | RT | 69.8429 | 71.4286 | 73.3429
|  | kBtu/h | 834.2 | 853 | 876.8
|  | kcal/h | 210270 | 215000 | 221020
| Power input | kW | 62.4 | 64.02 | 66.05
| COP | kW/kW | 3.9183 | 3.905 | 3.891
DC inverter compressor | Model |  | E705DHD-72D2YG×7 | E405DHD-36D2YG×2+ E705DHD-72D2YG×6 | E405DHD-42D2YG×2+ E705DHD-72D2YG×6
| Quantities |  | 7 | 8 | 8
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | 23.25+(23.25×2)×3 | (11.8+23.25)×2+(23.25×2)×2 | 13.8×2+(23.25×2)×3
|  | kBtu/h | 79.3+(79.3×2)×3 | (40.3+79.3)×2+(79.3×2)×2 | 47.1×2+(79.3×2)×3
| Crankcase heater | W | 27.6×14 | 27.6×16 | 27.6×16
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×7(500×7) | 0.132×8(500×8) | 0.132×8(500×8)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 7 | 8 | 8
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | 580+(550+430)×3 | (520+440)×2+(550+430)×2 | 360+290+(550+430)×3
| Output | W | 465+(440+350)×3 | (420+350)×2+(440+350)×2 | (290+230)+(440+350)×3
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 7 | 8 | 8
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 57300 | 62000 | 60500
|  | CFM | 33720 | 36480 | 35600
Sound pressure level |  | dB(A) | 69 | 70 | 70
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 39×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×3 | (52-3/4×64-3/8×31-1/8)×2 +(52-3/4×64-3/8×31-1/8)×2 | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×3
|  | mm | 990×1635×790+ (1340×1635×790)×3 | (1340×1635×790)×2 +(1340×1635×790)×2 | 1340×1635×790+ (1340×1635×790)×3
| Packing(W×H×D) | inch | 41-1/2×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×3 | (55-3/8×71-1/16×33-5/8)×2 +(55-3/8×71-1/16×33-5/8)×2 | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×3
|  | mm | 1055×1805×855+ (1405×1805×855)×3 | (1405×1805×855)×2 +(1405×1805×855)×2 | 1405×1805×855+ (1405×1805×855)×3
| Net weight | lbs.(kg) | 523+750×3(237+340×3) | 673×2+750×2(305×2+340×2) | 655+750×3(297+340×3)
| Gross weight | lbs.(kg) | 556+790×3(252+358×3) | 712×2+323×2(323×2+358×2) | 695+790×3(315+358×3)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 24+35×3(11+16×3) | 29×2+35×2(13×2+16×2) | 29+35×3(13+16×3)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ1(Φ25.4) | Φ1(Φ25.4) | Φ1(Φ25.4)
| Gas pipe | in.(mm) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## 84~88HP
|  |  | 84 | 86 | 88
Model | Combination Unit |  | MV5-X2125W/V2GN1 | MV5-X2180W/V2GN1 | MV5-X2230W/V2GN1
| Independent Unit |  | MV5-X500W/V2GN1 | MV5-X560W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
|  |  | MV5-X615W/V2GN1 | MV5-X615W/V2GN1 | MV5-X615W/V2GN1
Power source |  | V-Ph-Hz | 380～415V 3N 50Hz/60Hz
Cooling | Capacity | kW | 234.5 | 240.5 | 246
|  | RT | 67.0143 | 68.7143 | 70.2857
|  | kBtu/h | 800 | 820.5 | 839.2
|  | kcal/h | 201670 | 206830 | 211560
| Power input | kW | 70.78 | 72.98 | 75.08
| EER | kW/kW | 3.3131 | 3.2954 | 3.2765
Heating | Capacity | kW | 263 | 270 | 276
|  | RT | 75.1429 | 77.1429 | 78.8571
|  | kBtu/h | 897.3 | 921.1 | 941.6
|  | kcal/h | 226180 | 232200 | 237360
| Power input | kW | 67.73 | 69.56 | 71.44
| COP | kW/kW | 3.8831 | 3.8815 | 3.8634
DC inverter compressor | Model |  | E405DHD-36D2YG+ E705DHD-72D2YG×7 | E705DHD-72D2YG×8 | E705DHD-72D2YG×8
| Quantities |  | 8 | 8 | 8
| Type |  | DC inverter | DC inverter | DC inverter
| Brand |  | Hitachi | Hitachi | Hitachi
| Capacity | kW | (11.8+23.25)+(23.25×2)×3 | 23.25×2+(23.25×2)×3 | (23.25×2)×4
|  | kBtu/h | (40.3+79.3)+(79.3×2)×3 | 79.3×2+(79.3×2)×3 | (79.3×2)×4
| Crankcase heater | W | 27.6×16 | 27.6×16 | 27.6×16
| Refrigerant oil type |  | FVC68D | FVC68D | FVC68D
| Refrigerant oil charge | gal. (ml) | 0.132×8(500×8) | 0.132×8(500×8) | 0.132×8(500×8)
Outdoor fan motor | Model |  | WZDK560-38G(B) | WZDK560-38G(B) | WZDK560-38G(B)
| Type |  | DC motor | DC motor | DC motor
| Brand |  | Panasonic/Nidec | Panasonic/Nidec | Panasonic/Nidec
| Quantities |  | 8 | 8 | 8
| Insulation class |  | E | E | E
| Safe class |  | IP23 | IP23 | IP23
| Input | W | (520+440)+(550+430)×3 | (550+430)+(550+430)×3 | (550+430)×4
| Output | W | (420+350)+(440+350)×3 | (440+350)+(440+350)×3 | (440+350)×4
Outdoor fan | Material |  | Plastic | Plastic | Plastic
| Type |  | Axial | Axial | Axial
| Fan Quantities |  | 8 | 8 | 8
| External static pressure | in. W.G.(Pa) | 0～0.08(0~20) (default)
|  | in. W.G.(Pa) | 0.08~0.16(20~40) (customized)
Outdoor coil | Tube pitch(a) ×row pitch(b) | in.(mm) | 7/8×3/4(22×19) | 7/8×3/4(22×19) | 7/8×3/4(22×19)
| Fin spacing | in.(mm) | 1/16(1.6) | 1/16(1.6) | 1/16(1.6)
| Fin type |  | Hydrophilic aluminum
| Tube outside diameter | in.(mm) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94) | Ф5/16(Ф7.94)
| Tube type |  | Inner-grooved | Inner-grooved | Inner-grooved
Outdoor air flow |  | m3/h | 62000 | 62000 | 62000
|  | CFM | 36480 | 36480 | 36480
Sound pressure level |  | dB(A) | 70 | 70 | 70
Connectable indoor unit | Total capacity | % | 50-130 | 50-130 | 50-130
| Max. quantity |  | 64 | 64 | 64
Outdoor unit | Dimension(W×H×D) | inch | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×3 | 52-3/4×64-3/8×31-1/8+ (52-3/4×64-3/8×31-1/8)×3 | (52-3/4×64-3/8×31-1/8)×4
|  | mm | 1340×1635×790+ (1340×1635×790)×3 | 1340×1635×790+ (1340×1635×790)×3 | (1340×1635×790)×4
| Packing(W×H×D) | inch | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×3 | 55-3/8×71-1/16×33-5/8+ (55-3/8×71-1/16×33-5/8)×3 | (55-3/8×71-1/16×33-5/8)×4
|  | mm | 1405×1805×855+ (1405×1805×855)×3 | 1405×1805×855+ (1405×1805×855)×3 | (1405×1805×855)×4
| Net weight | lbs.(kg) | 673+750×3(305+340×3) | 750+750×3(340+340×3) | 750×4(340×4)
| Gross weight | lbs.(kg) | 712+790×3(323+358×3) | 790+790×3(358+358×3) | 790×4(358×4)
Refrigerant | Type |  | R410A | R410A | R410A
| Factory charged | lbs.(kg) | 29+35×3(13+16×3) | 35+35×3(16+16×3) | 35×4(16×4)
Throttle type |  |  | EXV | EXV | EXV
Design pressure(High/low) |  | Mpa | 4.4/2.6 | 4.4/2.6 | 4.4/2.6
|  | psi | 640/380 | 640/380 | 640/380
Pipe connections | Liquid pipe | in.(mm) | Φ1(Φ25.4) | Φ1(Φ25.4) | Φ1(Φ25.4)
| Gas pipe | in.(mm) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5) | Φ1-3/4(Φ44.5)
| Oil balance pipe | in.(mm) | Φ1/4(Φ6) | Φ1/4(Φ6) | Φ1/4(Φ6)
Operating temperature range | Cooling | °F(°C) | 23~118.4(-5~48)
| Heating | °F(°C) | -4~75.2(-20~24)
Notes: Capacities are based on the following conditions: Cooling: Indoor temperature 27℃(80.6℉) DB/19℃(66.2℉) WB; Outdoor temperature 35℃(95℉) DB/24℃(75.2℉) WB Heating: Indoor temperature 20℃(68℉) DB/15℃(59℉) WB; Outdoor temperature 7℃(44.6℉) DB/6℃(42.8℉) WB Piping length: Interconnecting piping length is 7.5m, level difference is zero.

## Sheet1
MV5-X252W/V2GN1 | 58 | 220095103940
MV5-X280W/V2GN1 | 59 | 220095103930
MV5-X335W/V2GN1 | 60 | 220095103950
MV5-X400W/V2GN1 | 62 | 220095103960
MV5-X450W/V2GN1 | 62 | 220095103970
MV5-X500W/V2GN1 | 63 | 220095103980
MV5-X560W/V2GN1 | 63 | 220095103990
MV5-X615W/V2GN1 | 63 | 220095104000