## A
Model MKA- |  |  | 600R(A) | 750R(A) | 850R(A) | 950R(A) | 1200R(A) | 1500R
Air Volume | High | m3/h | 1000 | 1250 | 1400 | 1600 | 2000 | 2550
|  | CFM | 590 | 740 | 820 | 940 | 1180 | 1500
| Med | m3/h | 850 | 1060 | 1190 | 1360 | 1700 | 2170
|  | CFM | 500 | 620 | 700 | 800 | 1000 | 1280
| Low | m3/h | 720 | 900 | 1010 | 1150 | 1440 | 1840
|  | CFM | 420 | 530 | 590 | 680 | 850 | 1080
Cooling Capacity (Hi/Med/Lo) |  | kW | 5.7/4.73/3.96 | 7.0/5.62/4.72 | 7.27/6.46/5.71 | 8.22/7.39/6.54 | 10.39/9.25/8.2 | 12.9/11.51/10.21
Heating Capacity (Hi/Med/Lo) |  | kW | 9.66/7.72/6.27 | 11.55/9.24/7.51 | 12.42/9.93/8.07 | 13.85/11.08/9 | 17.58/14.06/11.42 | 17.6/14.08/11.44
Electrical Auxiliary Heater (EAH) |  | W | 2100 | 2100 | 2850 | 2850 | 2850 | /
Power Input |  | W | 125 | 130 | 150 | 155 | 190 | 190
Noise (Hi/Med/Lo) |  | dB(A) | 45/41/36 | 46/42/37 | 47/43/38 | 48/44/39 | 49/45/40 | 50/46/41
Water Flow |  | L/min | 16.4 | 20 | 20.8 | 23.6 | 29.8 | 36.9
Water Pressure Drop |  | kPa | 23.8 | 25.2 | 27 | 31.2 | 44 | 40
Fan Motor | Type | \ | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Model | \ | YDK80-6E | YDK80-6E | YDK90-6E | YDK90-6E | YDK90-6E | YDK90-6E-1
| Brand | \ | Welling | Welling | Welling/Dayang | Welling/Dayang | Welling/Dayang | Welling/Dayang
| Capacitor | μF | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| Quantity | \ | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type | \ | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity | \ | 1 | 1 | 1 | 1 | 1 | 1
Coil | Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
| Row | \ | 2 | 2 | 2 | 2 | 2 | 3
| Tube pitch(a) x row pitch(b) | mm | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37
| Fin spacing | mm | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Fin type | \ | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum
| Coil length x height x width | mm | 1960×168×26.74 | 1960×168×26.74 | 1960×252×26.74 | 1960×252×26.74 | 1960×252×26.74 | 2080x252x40.11
| Max. Working Pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Circuit | \ | 8 | 8 | 12 | 12 | 12 | 12
Panel | Net Dimension (W×H×D) | mm | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950
| Net Weight | kg | 6 | 6 | 6 | 6 | 6 | 6
| Packing Size (W×H×D) | mm | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035
| Gross Weight | kg | 9 | 9 | 9 | 9 | 9 | 9
Indoor Unit | Net Dimension (W×H×D) | mm | 840×230×840 | 840×230×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840
| Net Weight (without/with EAH) | kg | 25/27 | 25/27 | 30.5/33 | 30.5/33 | 30.5/33 | 35
| Packing Size (W×H×D) | mm | 900×237×900 | 900×237×900 | 900×307×900 | 900×307×900 | 900×307×900 | 900×307×900
| Gross Weight (without/with EAH) | kg | 30/32 | 30/32 | 36.2/39 | 36.2/39 | 36.2/39 | 41
Pipe Connection | Water-inlet/outlet pipe | inch | RC3/4" | RC3/4" | RC3/4" | RC3/4" | RC3/4" | RC3/4"
| Drain pipe | mm | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32
Note:
1.The data is the performance in high speed with relevant static pressure.
2.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB,19°C WB.
Heating Conditions: Entering Water 50°C, Enter Air Temperature 20°C, and water flow is same to the cooling conditions.
3.Noise is tested in full-anechoic test room.

## AF
Model MKA- |  |  | 600F | 750F | 850F | 950F | 1200F | 1500F
Air volume | High speed | m3/h | 1150 | 1460 | 1480 | 1720 | 1860 | 2100
|  | CFM | 680 | 860 | 870 | 1010 | 1090 | 1230
| Mid speed | m3/h | 800 | 1020 | 1040 | 1200 | 1300 | 1470
|  | CFM | 470 | 600 | 610 | 700 | 760 | 860
| Low speed | m3/h | 690 | 880 | 890 | 1030 | 1110 | 1260
|  | CFM | 410 | 510 | 520 | 610 | 650 | 740
Cooling capacity |  | W | 5100 | 5930 | 6170 | 6700 | 9280 | 10580
Heating capacity |  | W | 6670 | 7870 | 8060 | 8670 | 11650 | 12620
Power supply |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | W | 170 | 188 | 198 | 205 | 197 | 234
Sound level (Hi/Med/Lo) |  | dB(A) | 42/32/26 | 43/34/28 | 46/36/30 | 47/38/32 | 48/40/34 | 50/42/36
Cooling | Water flow | L/min | 14.6 | 17 | 17.7 | 19.2 | 26.6 | 30.3
| Water pressure drop | kPa | 15 | 17 | 20 | 22 | 32 | 38
Heating | Water flow | L/min | 9.6 | 11.3 | 11.6 | 12.4 | 16.7 | 18.1
| Water pressure drop | kPa | 37 | 41 | 39 | 42 | 57 | 61
Fan | Type | \ | Centrifugal fan | Centrifugal fan | Centrifugal fan | Centrifugal fan | Centrifugal fan | Centrifugal fan
| Quantity | \ | 1 | 1 | 1 | 1 | 1 | 1
Motor | Model | \ | YDK56-6-1 | YDK56-6-1 | YDK90-6E | YDK90-6E | YDK90-6E-1 | YDK90-6E-1
| Quantity | \ | 1 | 1 | 1 | 1 | 1 | 1
| Capacitor | \ | 3μF/450V | 4μF/450V | 2.5μF/450V | 3μF/450V | 4μF/450V | 4μF/450V
Coil | Number of rows | \ | 2 | 2 | 2 | 2 | 3 | 3
| Tube pitch(a) × row pitch(b) | mm | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37
| Fin spacing | mm | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Fin type (code) | \ | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum
| Tube outside dia. | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
| Coil length × height | mm | 1990×252 | 1990×252 | 1990×252 | 1990×252 | 2080×252 | 2080×252
| Number of circuits | \ | 9 for cold water; 3 for hot water | 9 for cold water; 3 for hot water | 9 for cold water; 3 for hot water | 9 for cold water; 3 for hot water | 14 for cold water; 4 for hot water | 14 for cool water; 4 for heat water
| Max. Working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Test pressure | MPa | 1 | 1 | 1 | 1 | 1 | 1
Pipe Connection | Water-inlet pipe | inch | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2”
| Water-outlet pipe | inch | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2” | Cold water:RC3/4” Hot water:RC1/2”
| Drain pipe | mm | Φ32 | Φ32 | Φ32 | Φ32 | Φ32 | Φ32
Body | Net dimension (W×H×D) | mm | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840
| Packing dimension (W×H×D) | mm | 900×330×900 | 900×330×900 | 900×330×900 | 900×330×900 | 900×330×900 | 900×330×900
| Net weight | kg | 35 | 35 | 35 | 35 | 38 | 38
| Packing weight | kg | 41 | 41 | 41 | 41 | 44 | 44
Panel | Net dimension (W×H×D) | mm | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950
| Packing dimension (W×H×D) | mm | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035
| Net weight | kg | 6 | 6 | 6 | 6 | 6 | 6
| Packing weight | kg | 9 | 9 | 9 | 9 | 9 | 9
Control ( Wireless remote controller ) |  | \ | R05/BGE | R05/BGE | R05/BGE | R05/BGE | R05/BGE | R05/BGE
Note:
1.The data is the performance in high speed.
2.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB, 19°CWB.
Heating Conditions: Entering Water 70°C, Entering/Leaving temperature difference is 10°C, enter air temperature 20°C.
3.Noise level is tested in semi-anechoic room.

## D
Model MKD- |  |  | 300 | 400 | 500
Air Volume | High | m3/h | 510 | 680 | 850
|  | CFM | 300 | 400 | 500
| Med | m3/h | 440 | 580 | 730
|  | CFM | 260 | 340 | 430
| Low | m3/h | 360 | 480 | 600
|  | CFM | 210 | 280 | 350
Cooling Capacity (Hi/Med/Lo) |  | kW | 3/2.58/2.16 | 3.7/3.18/2.66 | 4.5/3.6/3.06
Heating Capacity (Hi/Med/Lo) |  | kW | 4/3.5/3.08 | 5.1/4.3/3.83 | 6/4.76/4.07
Power Input |  | W | 50 | 70 | 95
Noise (Hi/Med/Lo) |  | dB(A) | 36/33/28 | 42/39/32 | 45/42/34
Water Flow |  | L/min | 8.7 | 10.7 | 12.9
Water Pressure Drop |  | kPa | 14 | 15 | 16
Fan Motor | Type | \ | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Model | \ | YDK15-6P | YDK37-4P | YDK37-4P
| Brand | \ | Welling
| Capacitor | \ | 1.5 | 2 | 2.5
| Quantity | \ | 1 | 1 | 1
Fan | Type | \ | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity | \ | 1 | 1 | 1
Coil | Diameter | mm | Φ7 | Φ7 | Φ7
| Row | \ | 2 | 2 | 2
| Tube pitch(a) x row pitch(b) | \ | 21×13.37 | 21×13.37 | 21×13.37
| Fin spacing | \ | 1.3 | 1.3 | 1.3
| Fin type | \ | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum
| Length x Height x Width | \ | 1315×210×26.74 | 1315×210×26.74 | 1315×210×26.74
| Max. Working Pressure | MPa | 1.6 | 1.6 | 1.6
| Circuit | \ | 5 | 6 | 7
Panel | Net Dimension (W×H×D) | mm | 647×50×647 | 647×50×647 | 647×50×647
| Net Weight | kg | 3 | 3 | 3
| Packing Size (W×H×D) | mm | 715×123×715 | 715×123×715 | 715×123×715
| Gross Weight | kg | 5 | 5 | 5
Indoor Unit | Net Dimension (W×H×D) | mm | 575×261×575 | 575×261×575 | 575×261×575
| Net Weight | kg | 16.5 | 16.5 | 16.5
| Packing Size (W×H×D) | mm | 655×290×655 | 655×290×655 | 655×290×655
| Gross Weight | kg | 20 | 20 | 20
Pipe Connection | Water-inlet pipe | inch | RC3/4" | RC3/4" | RC3/4"
| Water-outlet pipe | inch | RC3/4" | RC3/4" | RC3/4"
| Drain pipe | mm | ODΦ25 | ODΦ25 | ODΦ25
Note:
1.The data is the performance in high speed with relevant static pressure.
2.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB,19°C WB.
Heating Conditions: Entering Water 50°C, enter air temperature 20°C, water flow is same to the cooling conditions.
3.Noise is tested in full-anechoic test room.

## C
Model MKC- |  |  |  | 300R-B | 400R-B | 600HRN4
|  |  |  | 300RA-B | 400RA-B
Air flow |  | H/M/L | m3/h | 510/450/400 | 630/560/500 | 1000/880/800
|  | H/M/L | CFM | 300/270/240 | 370/330/300 | 590/520/470
Cooling | Capacity | H/M/L | kW | 3.04/2.79/2.56 | 3.79/3.58/3.38 | 5.709/4.85/4.36
| Water flow rate | H | L/h | 520 | 650 | 982
| Water pressure drop | H | kPa | 14 | 20 | 20.2
Heating | Capacity | H/M/L | kW | 5.13/4.69/4.04 | 6.41/5.86/5.11 | 9.6/8.36/7.48
| Water pressure drop | H | kPa | 9 | 16 | 18.1
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | H | W | 32 | 40 | 125
Electric heater capacity |  |  | W | 750 | 750 | /
Sound pressure level |  | H/M/L | dB(A) | 36/34//32 | 37/35/34 | 42/39/37
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1
Fan | Type |  |  | Cross fan | Cross fan | Centrifugal fan
| Quantity |  |  | 1 | 1 | 4
Coil | Row |  |  | 2 | 2 | 3
| Max. Working pressure |  | MPa | 1.6 | 1.6
| Diameter |  | mm | Φ7 | Φ7 | Φ8
Panel | Dimensions | W×H×D | mm | 1180x25x465 | 1180x25x465 | 1420×10×755
| Packing | W×H×D | mm | 1232x107x517 | 1232x107x517 | 1500×110×870
| Net weight |  | kg | 3.5 | 3.5 | 9
| Gross weight |  | kg | 5.2 | 5.2 | 12
Body | Dimensions | W×H×D | mm | 1054x169x425 | 1054x169x425 | 1200×198×655
| Net weight | */A | kg | 12.8/13.1 | 12.8/13.1 | 32.6
| Packing | W×H×D | mm | 1155x245x490 | 1155x245x490 | 1380×265×720
| Gross weight | */A | kg | 16.6/17.1 | 16.6/17.1 | 36.3
Pipe connection | Water inlet/outlet pipe |  | inch | G1/2 | G1/2 | RC3/4
| Drain pipe |  | mm | ODΦ25 | ODΦ25 | ODΦ20
Note:
1.H: High fan speed; M: Medium fan speed; L: Low fan speed.
2.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB.
Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions.
3.Noise is tested in a semi-anechoic test room.
4.* for models without electric heater, A for models with electric heater.

## T2
Model MKT2- |  |  |  | 200G12 | 300G12 | 400G12 | 500G12 | 600G12 | 800G12 | 1000G12 | 1200G12 | 1400G12
|  |  |  | 200G30 | 300G30 | 400G30 | 500G30 | 600G30 | 800G30 | 1000G30 | 1200G30 | 1400G30
|  |  |  | 200EG30 | 300EG30 | 400EG30 | 500EG30 | 600EG30 | 800EG30 | 1000EG30 | 1200EG30 | 1400EG30
Air flow |  | H/M/L | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020 | 2380/1785/1190
|  | H/M/L | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600 | 1400/1050/700
External Static pressure |  |  | Pa | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30
Cooling | Capacity | H/M/L | kW | 2/1.74/1.52 | 2.7/2.31/2.03 | 3.6/3.11/2.66 | 4.4/3.74/3.25 | 5.5/4.58/4.09 | 7.5/6.33/5.68 | 8.9/7.61/6.41 | 10.8/9.13/7.93 | 12.3/10.46/9.27
| Water flow rate | H | L/h | 344 | 464 | 619 | 757 | 946 | 1290 | 1531 | 1858 | 2116
| Water pressure drop | H | kPa | 5 | 11 | 19 | 22 | 14 | 14 | 22 | 39 | 46
Heating | Capacity | H/M/L | kW | 3.2/2.75/2.37 | 4.3/3.74/3.23 | 5.4/4.64/4.05 | 6.8/5.78/5.07 | 8.1/6.77/5.92 | 11/9.48/8.25 | 13.5/11.72/10.03 | 16.5/14.05/12.24 | 19.5/16.85/14.63
| Water pressure drop | H | kPa | 4.2 | 9.5 | 15.5 | 18.3 | 11.8 | 12.5 | 19 | 32.6 | 40.1
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input | 12Pa | H | W | 31 | 50 | 60 | 80 | 97 | 140 | 172 | 205 | 216
| 30Pa | H | W | 45 | 60 | 67 | 89 | 110 | 130 | 171 | 212 | 249
Electric heater capacity |  | E | W | 550 | 650 | 1100 | 1100 | 1600 | 2200 | 2200 | 3200 | 3200
Sound | 12Pa | H/M/L | dB(A) | 36/34/29 | 38/33/29 | 38/35/31 | 39/36/32 | 40/36/33 | 42/37/33 | 44/39/34 | 46/40/35 | 48/42/37
pressure level | 30Pa | H/M/L | dB(A) | 41/37/31 | 41/37/32 | 42/39/33 | 45/41/34 | 46/41/35 | 46/41/36 | 47/43/37 | 48/44/38 | 49/44/39
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4
Coil | Row |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Max. working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522 | 2022×241×522
| Packing | W×H×D | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550 | 2070×260×550
| Net weight | */E | kg | 13.9/14.5 | 16.5/18 | 19.2/20.7 | 19.2/20.7 | 22/24 | 30.9/33.4 | 33.4/36.4 | 38.5/42 | 42.1/46.1
| Gross weight | */E | kg | 16.2/17.7 | 19/20.5 | 21.6/23.1 | 21.6/23.1 | 25/27 | 34.5/37 | 37/40 | 42/45.5 | 47.5/51.5
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note：
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.* for units without electric heater, E for units with electric heater.
3.The data is based on 12Pa external static pressure for G12 models, 30Pa for G30 models.
4.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: entering water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
5.Noise is tested in semi-anechoic test room.

## T3
Model MKT3- |  |  |  | 200G12 | 300G12 | 400G12 | 500G12 | 600G12 | 800G12 | 1000G12 | 1200G12 | 1400G12
|  |  |  | 200G30 | 300G30 | 400G30 | 500G30 | 600G30 | 800G30 | 1000G30 | 1200G30 | 1400G30
|  |  |  | 200EG30 | 300EG30 | 400EG30 | 500EG30 | 600EG30 | 800EG30 | 1000EG30 | 1200EG30 | 1400EG30
Air flow |  | H/M/L | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020 | 2380/1785/1190
|  | H/M/L | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600 | 1400/1050/700
External Static pressure |  |  | Pa | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30
Cooling | Capacity | H/M/L | kW | 2.2/1.9/1.68 | 3.1/2.7/2.3 | 4/3.4/2.95 | 4.6/3.96/3.45 | 5.8/4.88/4.45 | 8.2/6.88/6.25 | 9/7.8/6.57 | 11/9.8/8.35 | 12.5/10.8/9.44
| Water flow rate | H | L/h | 378 | 533 | 688 | 791 | 998 | 1410 | 1548 | 1892 | 2150
| Water pressure drop | H | kPa | 14 | 26 | 18 | 24 | 36 | 39 | 32 | 39 | 45
Heating | Capacity | H/M/L | kW | 3.5/3.08/2.59 | 5.3/4.61/3.98 | 6.8/5.85/5.1 | 7.9/6.95/6 | 9.8/8.6/7.4 | 13.6/11.97/10.2 | 16/14.24/12 | 20.1/18.27/15.43 | 21/18.7/15.75
| Water pressure drop | H | kPa | 10.5 | 21.8 | 16.9 | 22.3 | 31.6 | 33.8 | 30.7 | 34.6 | 40.1
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input | 12Pa | H | W | 33 | 53 | 66 | 87 | 100 | 145 | 180 | 210 | 222
| 30Pa | H | W | 49 | 64 | 75 | 93 | 114 | 154 | 180 | 220 | 278
Electric heater capacity |  | E | W | 550 | 650 | 1100 | 1100 | 1600 | 2200 | 2200 | 3200 | 3200
Sound | 12Pa | H/M/L | dB(A) | 35/32/26 | 36/33/27 | 37/34/28 | 40/36/30 | 42/38/32 | 43/39/33 | 45/41/35 | 46/42/36 | 48/44/38
pressure level | 30Pa | H/M/L | dB(A) | 41/37/31 | 42/38/32 | 43/39/33 | 44/40/34 | 45/41/35 | 46/42/36 | 47/43/37 | 48/44/38 | 49/45/39
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4
Coil | Row |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Max. working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522 | 2022×241×522
| Packing | W×H×D | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550 | 2070×260×550
| Net weight | */E | kg | 14.6/16.1 | 17/18.5 | 20.2/21.7 | 20.2/21.7 | 23/25 | 31.9/34.4 | 34.4/37.4 | 39.5/43 | 43.1/47.1
| Gross weight | */E | kg | 16.9/18.4 | 19.5/21 | 22.6/24.1 | 22.6/24.1 | 26/28 | 35.5/38 | 38.1/41.1 | 43/46.5 | 48.4/52.4
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note：
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.* for units without electric heater, E for units with electric heater.
3.The data is based on 12Pa external static pressure for G12 models, 30Pa for G30 models.
4.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: entering water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
5.Noise is tested in semi-anechoic test room.

## T4
Model MKT4- |  |  |  | 200G30 | 300G30 | 400G30 | 500G30 | 600G30 | 800G30 | 1000G30 | 1200G30 | 1400G30 | 1500 | H-1500G50 | 2000 | H-2000G50
Air flow |  | H/M/L | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020 | 2380/1785/1190 | 2550/2100/1300 | 2550/2100/1300 | 3400/2550/1700 | 3400/2550/1700
|  | H/M/L | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600 | 1400/1050/700 | 1500/1240/760 | 1500/1240/760 | 2000/1500/1000 | 2000/1500/1000
External Static pressure |  |  | Pa | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 30 | 50
Cooling | Capacity | H/M/L | kW | 2.5/2.16/1.87 | 3.3/2.85/2.47 | 4.4/3.72/3.22 | 4.8/4.18/3.64 | 6.2/5.38/4.65 | 8.8/7.43/6.57 | 9.5/8.18/7.06 | 11.8/9.82/8.74 | 13/11.23/9.83 | 13.5/11.5/10.1 | 13.5/11.5/10.1 | 18/15.3/13.5 | 18/15.3/13.5
| Water flow rate | H | L/h | 430 | 568 | 757 | 826 | 1066 | 1514 | 1634 | 2030 | 2236 | 2322 | 2322 | 3096 | 3096
| Water pressure drop | H | kPa | 2.6 | 5 | 8.1 | 9.8 | 15.4 | 12.3 | 18 | 21.2 | 24.7 | 11.5 | 11.5 | 26.2 | 26.2
Heating | Capacity | H/M/L | kW | 4.1/3.51/3.03 | 5.8/5.05/4.35 | 7.1/6.11/5.33 | 8.5/7.04/6.28 | 10.5/9.03/7.77 | 14.5/12.38/10.88 | 16.3/13.45/12.05 | 16.5/14.05/12.23 | 17/14.31/12.69 | 17.5/14.9/13.2 | 17.5/14.9/13.2 | 23.4/19.8/17.5 | 23.4/19.8/17.5
| Water pressure drop | H | kPa | 2.2 | 4.2 | 6.9 | 8.1 | 12.7 | 10 | 15.4 | 17.6 | 20.8 | 10 | 10 | 24.3 | 24.3
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | H | W | 50 | 65 | 80 | 95 | 110 | 155 | 180 | 220 | 275 | 236 | 474 | 360 | 665
Sound pressure level |  | H/M/L | dB(A) | 37/33/27 | 38/34/28 | 38/35/29 | 40/35/30 | 41/36/31 | 42/37/32 | 44/39/33 | 45/40/34 | 47/42/36 | 48/44/39 | 51/47/42 | 50/46/41 | 53/49/44
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 2 | 2 | 3 | 3
Coil | Row |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Max. Working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522 | 2022×241×522 | 1369×342×612 | 1369×342×612 | 1500×342×612 | 1500×342×612
| Net weight |  | kg | 15.3 | 17.5 | 20.7 | 20.7 | 23.5 | 32.9 | 35.4 | 40.5 | 44.1 | 1421×381×619 | 1421×381×619 | 1552×381×619 | 1552×381×619
| Packing | W×H×D | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550 | 2070×260×550 | 46 | 46 | 57 | 53.7
| Gross weight |  | kg | 17.6 | 20 | 23.1 | 23.1 | 26.5 | 36.5 | 39.1 | 44 | 49.4 | 49.8 | 50 | 61 | 58.6
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note:
1.H: high speed; M: medium speed; L: low speed.
2.The data is based on 30Pa external static pressure.
3.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: entering water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
4.Noise is tested in semi-anechoic test room.

## A4
Model MKT3- |  |  |  | 800G50-A4 | 1000G50-A4
Air flow |  | H/M/L | m3/h | 1500/1412/1265 | 1700/1664/1554
|  | H/M/L | CFM | 890/831/745 | 1000/980/915
External Static pressure |  |  | Pa | 50 | 50
Cooling | Capacity | H/M/L | kW | 6.97/6.66/6.28 | 7.77/7.58/7.33
| Water flow rate | H | L/h | 1198 | 1336
| Water pressure drop | H | kPa | 19 | 24.5
Heating | Capacity | H/M/L | kW | 9.57/9.09/8.43 | 10.61/10.25/9.82
| Water pressure drop | H | kPa | 16.9 | 21.1
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50
Power input |  | H/M/L | W | 151/130/111 | 174/147/130
Sound pressure level |  | H/M/L | dB(A) | 49.7/47.8/45.6 | 50.1/48/45.8
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Model |  |  | YSK105-6SC | YSK150-6SC
| Quantity |  |  | 1 | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 2 | 2
Coil | Row |  |  | 3 | 3
| Max. Working pressure |  | MPa | 1.6 | 1.6
| Coil length x height |  | mm | 885x305 | 885x305
| Fin spacing |  | mm | 2.2 | 2.2
| Fin type |  |  | Hydrophilic aluminum | Hydrophilic aluminum
| Number of circuits |  |  | 5 | 5
| Diameter |  | mm | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 1180×340×612 | 1180×340×612
| Packing | W×H×D | mm | 1310×380×693 | 1310×380×693
| Net weight |  | kg | 38.3 | 39.8
| Gross weight |  | kg | 47.2 | 48.6
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24
Note:
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.Cooling conditions: Entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: Entering water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
3.Noise is tested in semi-anechoic test room.
Model MKT4- |  |  |  | 800G50-A4 | 1000G50-A4 | 1200G50-A4 | 1400G50-A4 | 1600G50-A4 | 1800G50-A4 | 2000G50-A4
Air flow |  | H/M/L | m3/h | 1400/1342/1200 | 1650/1527/1405 | 2040/1851/1666 | 2420/1851/1666 | 2430/1917/1742 | 3380/2239/1878 | 3670/2544/2199
|  | H/M/L | CFM | 856/790/706 | 970/900/827 | 1206/1090/981 | 1427/1090/981 | 1431/1128/1025 | 1990/1318/1105 | 2160/1497/1294
External Static pressure |  |  | Pa | 50 | 50 | 50 | 50 | 50 | 50 | 50
Cooling | Capacity | H/M/L | kW | 7.92/7.56/7.09 | 8.15/7.93/7.54 | 10.8/10.17/9.55 | 12.14/10.17/9.55 | 12.19/10.54/9.87 | 16.16/12.35/11.01 | 17.34/13.75/12.44
| Water flow rate | H | L/h | 1363 | 1402 | 1890 | 2089 | 2096 | 2779 | 2983
| Water pressure drop | H | kPa | 48 | 21.4 | 27.8 | 32.5 | 33.4 | 58.3 | 61.5
Heating | Capacity | H/M/L | kW | 10.42/9.89/9.12 | 11.25/10.72/10.06 | 14.3/13.23/12.22 | 16.08/13.23/12.22 | 16.55/13.83/12.9 | 21.7/15.79/13.91 | 23.4/17.92/16.08
| Water pressure drop | H | kPa | 39.7 | 23.3 | 24.8 | 29.2 | 30 | 52.3 | 52.9
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | H/M/L | W | 144/124/105 | 176/146/128 | 320/284/250 | 392/284/250 | 482/338/296 | 538/358/308 | 583/387/334
Sound pressure level |  | H/M/L | dB(A) | 48.4/47.9/46.6 | 49.5/48.1/47.3 | 50.9/50/48.5 | 51.7/50/49.5 | 52.9/50.7/50 | 53.6/51.1/50.2 | 54.4/52.7/51.6
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Model |  |  | YSK105-6SC | YSK150-6SC | YSK230-4SC | YSK230-4SC | YSK230-4SC | YSK360-4SC | YSK360-4SC
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 2 | 2 | 2 | 2 | 2 | 3 | 3
Coil | Row |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Max. Working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Coil length x height |  | mm | 885x305 | 885x305 | 1085x305 | 1085x305 | 1085x305 | 1277x305 | 1277x305
| Fin spacing |  | mm | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
| Fin type |  |  | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum | Hydrophilic aluminum
| Number of circuits |  |  | 4 | 6 | 8 | 8 | 8 | 8 | 8
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 1180x340x612 | 1180x340x612 | 1369x340x612 | 1369x340x612 | 1369x340x612 | 1500x340x612 | 1500x340x612
| Packing | W×H×D | mm | 1310x380x693 | 1310x380x693 | 1490*380*693 | 1490*380*693 | 1490*380*693 | 1620x380x693 | 1620x380x693
| Net weight |  | kg | 39.3 | 40.8 | 46.3 | 46.3 | 46.3 | 54.8 | 54.8
| Gross weight |  | kg | 47 | 49.6 | 56.4 | 56.4 | 56.4 | 64.6 | 64.6
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note:
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.Cooling conditions: Entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: Entering water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
3.Noise is tested in semi-anechoic test room.

## T3H
Model MKT3H- |  |  |  | 800G70 | 1000G70 | 1200G70 | 1400G70 | 1600G100 | 1800G100 | 2200G100
|  |  |  | 800EG70 | 1000EG70 | 1200EG70 | 1400EG70 | 1600EG100 | 1800EG100 | 2200EG100
Air flow |  | H/M/L | m3/h | 1360/1220/1090 | 1700/1530/1380 | 2040/1880/1610 | 2380/2120/1860 | 2720/2450/2170 | 3060/2750/2450 | 3740/3360/2990
|  | H/M/L | CFM | 800/720/640 | 1000/900/810 | 1200/1105/950 | 1400/1250/1095 | 1600/1440/1280 | 1800/1620/1440 | 2200/1980/1760
External Static pressure |  |  | Pa | 70 | 70 | 70 | 70 | 100 | 100 | 100
Cooling | Capacity | H/M/L | kW | 6.6/6.37/6.12 | 8.8/8.19/7.57 | 10/9.44/8.53 | 12/11.47/10.24 | 14.1/13.03/11.87 | 15.8/14.6/13.46 | 19.9/18.58/17.24
| Water flow rate | H | L/h | 1135 | 1514 | 1720 | 2064 | 2425 | 2718 | 3423
| Water pressure drop | H | kPa | 8 | 24 | 24 | 36 | 52 | 90 | 130
Heating | Capacity | H/M/L | kW | 9.7/8.54/7.18 | 13.2/11.48/9.9 | 15/12.9/11.25 | 17.9/15.75/13.6 | 21.2/18.23/15.69 | 23.8/20.94/17.85 | 30/26.7/22.5
| Water pressure drop | H | kPa | 8.4 | 25 | 23.4 | 34.2 | 51 | 85 | 121
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | H | W | 350 | 350 | 350 | 350 | 550 | 800 | 950
Electric heater capacity ('E) |  |  | W | 5000 | 5000 | 5000 | 5000 | 9500 | 9500 | 9500
Sound pressure level |  | H/M/L | dB(A) | 49/42/35 | 50/43/36 | 51/44/37 | 52/45/38 | 54/47/40 | 60/53/46 | 61/54/47
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 | 1 | 1 | 1 | 2 | 2 | 2
Coil | Row |  |  | 2 | 3 | 3 | 4 | 3 | 3 | 3
| Max. Working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions (*/E) | W×H×D | mm | 946×400×816 / 946×400×876 | 946×400×816 / 946×400×876 | 946×400×816 / 946×400×876 | 946×400×816 / 946×400×876 | 1290×400×809 / 1290×400×874 | 1290×400×809 / 1290×400×874 | 1290×400×809 / 1290×400×874
| Net weight (*/E) |  | kg | 50/53 | 52/55 | 52/55 | 54/57 | 76/82 | 76/82 | 76/82
| Packing (*/E) | W×H×D | mm | 1015×480×857 / 1015×480×925 | 1015×480×857 / 1015×480×925 | 1015×480×857 / 1015×480×925 | 1015×480×857 / 1015×480×925 | 1368×460×877 / 1368×460×950 | 1368×460×877 / 1368×460×950 | 1368×460×877 / 1368×460×950
| Gross weight (*/E) |  | kg | 55/58 | 57/60 | 57/60 | 59/62 | 83/89 | 83/89 | 83/89
Pipe connection | Water inlet/outlet pipe |  | inch | RC3/4" | RC3/4" | RC3/4" | RC3/4" | RC3/4" | RC3/4" | RC3/4"
| Drain pipe |  | mm | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32
Note:
1.H: high speed; M: medium speed; L: low speed.
2.The data is the performance in 70Pa external static pressure.
3.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB,19°C WB.
Heating Conditions: Entering Water 50°C, Entering air temperature 20°C, the same water flow as the cooling conditions.
4.Noise is tested in semi-anechoic test room.
5.* for models without EAH; E for models with EAH.

## G
S Panel | [7 empty] | C Panel
Model MKG- |  |  | 250-B | 300-B | 400-B | 500-B | 600-B | Model MKG- |  |  |  | 250 | 300 | 400 | 500 | 600
Power supply |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | Air flow |  | H/M/L | m3/h | 425/360/320 | 510/430/380 | 680/580/510 | 850/720/640 | 1020/870/770
Air flow (H/M/L) |  | m3/h | 425/390/350 | 510/470/390 | 680/550/460 | 850/745/620 | 1020/915/780 |  |  | H/M/L | CFM | 250/210/190 | 300/250/220 | 400/340/300 | 500/420/380 | 600/510/450
|  | CFM | 250/230/205 | 300/275/230 | 400/325/270 | 500/440/365 | 600/540/460 | Cooling | Capacity | H/M/L | kW | 2.2/1.84/1.65 | 2.64/2.24/2.05 | 3.08/2.62/2.27 | 4.07/3.73/3.24 | 4.45/4.18/3.74 | 有问题，需要确认数据正确性
Cooling | Capacity (H/M/L) | kW | 2.63/2.41/2.16 | 2.97/2.47/2.12 | 3.28/2.83/2.41 | 4.25/3.85/3.32 | 5/4.47/3.97 |  | Water flow rate | H | L/h | 378 | 454 | 530 | 700 | 765
| Water flow rate | L/h | 452 | 511 | 564 | 731 | 860 |  | Water pressure drop | H | kPa | 12 | 18 | 22 | 26 | 29
| Water pressure drop | kPa | 29.4 | 35.6 | 43.5 | 31.8 | 42.5 | Heating | Capacity | H/M/L | kW | 3.02/2.6/2.23 | 3.69/3.25/2.77 | 4.34/3.86/3.25 | 5.69/5.12/4.32 | 6.3/5.67/4.73
Heating | Capacity (H/M/L) | kW | 3.36/3.1/2.79 | 3.91/3.26/2.77 | 4.37/3.73/3.17 | 5.81/5.17/4.43 | 6.7/6/5.28 |  | Water pressure drop | H | kPa | 10 | 16.4 | 20.8 | 25.1 | 27.9
| Water pressure drop | kPa | 27.3 | 32.9 | 40.8 | 30.2 | 39.7 | Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input |  | W | 24 | 37 | 40 | 50 | 66 | Power input |  | H | W | 28 | 40 | 44 | 50 | 60
Sound pressure level |  | dB(A) | 30/24/20 | 35/29/24 | 37/31/26 | 39/33/28 | 40/34/29 | Sound pressure level |  | H/M/L | dB(A) | 30/24/20 | 35/29/24 | 37/31/26 | 39/33/28 | 40/34/29
Fan motor | Type |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 |  | Quantity |  |  | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Tangential fan | Tangential fan | Tangential fan | Tangential fan | Tangential fan | Fan | Type |  |  | Cross-flow fan | Cross-flow fan | Cross-flow fan | Cross-flow fan | Cross-flow fan
| Quantity |  | 1 | 1 | 1 | 1 | 1 |  | Quantity |  |  | 1 | 1 | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2 | 2 | 2 | Coil | Row |  |  | 2 | 2 | 2 | 2 | 2
| Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7 |  | Max. Working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Tube pitch(a)xrow pitch(b) | mm | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 | 21×13.37 |  | Diameter |  | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
| Dimension (W×H×D) | mm | 635×315×26.74 | 635×315×26.74 | 635×315×26.74 | 785×315×26.74 | 785×315×26.74 | Body | Dimensions | W×H×D | mm | 915×210×290 | 915×210×290 | 915×210×290 | 1070×210×316 | 1070×210×316
| Fin spacing | mm | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | Net weight |  | kg | 12 | 12 | 12 | 15 | 15
| Fin type |  | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium |  | Packing | W×H×D | mm | 1020×300×385 | 1020×300×385 | 1020×300×385 | 1180×300×410 | 1180×300×410
| Circuit |  | 5 | 5 | 5 | 5 | 5 |  | Gross weight |  | kg | 16 | 16 | 16 | 19 | 19
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | Pipe connection | Water inlet/outlet pipe |  | inch | G3/4" | G3/4" | G3/4" | G3/4" | G3/4"
Body | Net dimensions (W×H×D) | mm | 915×290×230 | 915×290×230 | 915×290×230 | 1072×315×230 | 1072×315×230 |  | Drain pipe |  | mm | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20
| Packing size (W×H×D) | mm | 1020×390×315 | 1020×390×315 | 1020×390×315 | 1180×415×315 | 1180×415×315 | Controller |  |  |  | R51/E (standard) | R51/E (standard) | R51/E (standard) | R51/E (standard) | R51/E (standard)
| Net weight | kg | 13 | 13 | 13.3 | 15.8 | 15.8
| Gross weight | kg | 16.3 | 16.3 | 16.7 | 19.4 | 19.4 | Note:
Pipe connections | Water inlet/outlet pipe | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | 1.H: high speed; M: medium speed; L: low speed.
| Drain pipe | mm | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20 | 2.Cooling Conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating Conditions: entering water 50°C, Entering air temperature 20°C, the same water flow as the cooling conditions.
Note: | [7 empty] | 3.Noise is tested in semi-anechoic test room.
1.H: high speed; M: medium speed; L: low speed.
2.Cooling Conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating Conditions: entering water 50°C, Entering air temperature 20°C, the same water flow as the cooling conditions.
3.Noise is tested in semi-anechoic test room.

## H
Model |  |  | MKH3-150 | MKH3-250 | MKH3-300 | MKH3-400 | MKH3-450 | MKH3-500 | MKH3-600 | MKH3-800 | MKH3-900
|  |  | MKH4-150 | MKH4-250 | MKH4-300 | MKH4-400 | MKH4-450 | MKH4-500 | MKH4-600 | MKH4-800 | MKH4-900
|  |  | MKH5-150 | MKH5-250 | MKH5-300 | MKH5-400 | MKH5-450 | MKH5-500 | MKH5-600 | MKH5-800 | MKH5-900
Power supply |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 255/215/190 | 425/360/320 | 510/430/380 | 680/580/510 | 765/650/570 | 850/720/640 | 1020/870/765 | 1360/1160/1020 | 1530/1300/1150
|  | CFM | 150/125/110 | 250/210/190 | 300/250/220 | 400/340/300 | 450/380/335 | 500/420/375 | 600/510/450 | 800/680/600 | 900/760/675
External static pressure |  | Pa | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0. | H3 models: 12; H4/H5 models: 0.
Cooling | Capacity (H/M/L) | kW | 1.15/0.93/0.89 | 1.87/1.74/1.59 | 2.53/2.25/1.88 | 3.27/2.84/2.54 | 3.97/3.58/3.15 | 4.85/4.41/3.72 | 5.64/5.02/4.46 | 6.52/5.75/4.36 | 7.85/7.19/6.55
| Water flow rate | L/h | 198 | 322 | 435 | 562 | 683 | 834 | 970 | 1121 | 1350
| Water pressure drop | kPa | 18.3 | 10.1 | 14.2 | 26.3 | 23.1 | 20 | 11.4 | 21 | 24.3
Heating | Capacity (H/M/L) | kW | 1.52/1.29/1.14 | 2.53/2.15/1.90 | 3.49/2.97/2.62 | 4.58/3.89/3.44 | 5.64/4.79/4.23 | 6.98/5.93/5.24 | 8.23/7.00/6.17 | 9.58/8.14/7.19 | 11.69/9.94/8.77
| Water pressure drop | kPa | 16 | 8.8 | 13.7 | 24 | 22 | 17.4 | 10 | 20.2 | 21.5
Power input (H/M/L) |  | W | 27/22/19 | 29/23/20 | 40/32/28 | 46/37/32 | 39/31/27 | 49/39/34 | 63/50/44 | 88/70/62 | 137/109/96
Sound pressure level | H3 (H/M/L) | dB(A) | 30/27/24 | 33/30/28 | 35/32/30 | 37/34/32 | 39/36/34 | 41/38/36 | 42/39/37 | 44/41/38 | 46/43/40
| H4 (H/M/L) | dB(A) | 32/29/26 | 35/32/30 | 37/34/32 | 39/36/34 | 41/38/36 | 43/40/38 | 44/41/39 | 46/43/40 | 48/45/42
| H5 (H/M/L) | dB(A) | 30/27/24 | 33/30/28 | 35/32/30 | 37/34/32 | 39/36/34 | 41/38/36 | 42/39/37 | 44/41/38 | 46/43/40
Fan motor | Type |  | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
Coil | Row |  | 3 | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body (H3 series) | Net dimensions (W×H×D) | mm | 550×545×212 | 550×545×212 | 750×545×212 | 750×545×212 | 950×545×212 | 950×545×212 | 1250×545×212 | 1250×545×212 | 1250×545×212
| Packing size (W×H×D) | mm | 639×639×305 | 639×639×305 | 839×639×305 | 839×639×305 | 1039×639×305 | 1039×639×305 | 1339×639×305 | 1339×639×305 | 1339×639×305
| Net weight | kg | 17 | 17 | 20 | 20 | 25 | 25 | 32 | 32 | 32
| Gross weight | kg | 19 | 19 | 23.5 | 23.5 | 29 | 29 | 36 | 36 | 36
Body (H4/H5 series) | Net dimensions (W×H×D) | mm | 800×592×225 | 800×592×225 | 1000×592×225 | 1000×592×225 | 1200×592×225 | 1200×592×225 | 1500×592×225 | 1500×592×225 | 1500×592×225
| Packing size (W×H×D) | mm | 889×683×312 | 889×683×312 | 1089×683×312 | 1089×683×312 | 1289×683×312 | 1289×683×312 | 1589×683×312 | 1589×683×312 | 1589×683×312
| Net weight | kg | 22.5/22.5 | 22.5/22.5 | 26/26 | 26/26 | 32.5/32.5 | 32.5/32.5 | 39/39 | 39/39 | 39/39
| Gross weight | kg | 26.5/26.5 | 27/26.5 | 31/31 | 31/31 | 38/38 | 38/38 | 45/45 | 45/45 | 45/45
Water inlet/outlet pipe |  | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4
Drain pipe |  | mm | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16
Note：
1.H: High fan speed; M: Medium fan speed; L: Low fan speed.
2.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB.
Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions.
3.Noise is tested in a semi-anechoic test room.

## F
Model MKF3 (4,5)- |  |  | 150 | 250 | 300 | 400 | 450 | 500 | 600 | 800 | 900
Air Volume | Hi | m3/h | 255 | 425 | 510 | 680 | 765 | 850 | 1020 | 1360 | 1530
|  | CFM | 150 | 250 | 300 | 400 | 450 | 500 | 600 | 800 | 900
| Med | m3/h | 215 | 360 | 430 | 580 | 650 | 720 | 870 | 1160 | 1300
|  | CFM | 125 | 210 | 250 | 340 | 380 | 420 | 510 | 680 | 760
| Lo | m3/h | 190 | 320 | 380 | 510 | 570 | 640 | 765 | 1020 | 1150
|  | CFM | 110 | 190 | 220 | 300 | 335 | 375 | 450 | 600 | 675
External static pressure |  | Pa | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0. | F3 models: 12; F4/F5 models: 0.
Cooling Capacity |  | W | 1150 | 1870 | 2530 | 3270 | 3970 | 4850 | 5640 | 6520 | 7850
Heating Capacity |  | W | 2540 | 4170 | 5640 | 7220 | 8850 | 10280 | 12240 | 15350 | 18200
Power Input |  | W | 27 | 29 | 40 | 46 | 39 | 49 | 63 | 88 | 137
Noise(Hi/Med/Lo) |  | dB(A) | 32/29/26 | 35/32/30 | 37/34/32 | 39/36/34 | 41/38/36 | 43/40/38 | 44/41/39 | 46/43/40 | 48/45/42
Water Flow |  | L/min | 3.3 | 5.4 | 7.3 | 9.4 | 11.4 | 13.9 | 16.2 | 18.7 | 22.5
Water Pressure Drop |  | kPa | 18.3 | 10.1 | 14.2 | 9.5 | 10.3 | 24.6 | 11.4 | 9.5 | 12.1
Fan Motor | Type | \ | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor | Low noise 3-speed fan motor
| Model | \ | YDK18-6A | YDK18-6A | YSK20-4A | YSK20-4A | YSK20-6 | YSK20-6 | YSK28-4D | YSK28-4E | YSK74-4E
| Quantity | \ | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type | \ | Centrifugal, forward-curved Blades |  |  |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity | \ | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
Coil | Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
| Max. Working Pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Row | \ | 3 | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 2
| Circuit | \ | 2 | 2 | 2 | 2 | 3 | 3 | 4 | 4 | 4
Indoor Unit F3 | Net Dimension (W×H×D) | mm | 550×545×212 | 550×545×212 | 750×545×212 | 750×545×212 | 950×545×212 | 950×545×212 | 1250×545×212 | 1250×545×212 | 1250×545×212
| Net Weight | kg | 17 | 17 | 20 | 20 | 25 | 25 | 32 | 32 | 32
| Packing Size (W×H×D) | mm | 639×639×305 | 639×639×305 | 839×639×305 | 839×639×305 | 1039×639×305 | 1039×639×305 | 1339×639×305 | 1339×639×305 | 1339×639×305
| Gross Weight | kg | 19 | 19 | 23.5 | 23.5 | 29 | 29 | 36 | 36 | 36
Indoor Unit F4(5) | Net Dimension (W×H×D) | mm | 800×572×225 | 800×572×225 | 1000×572×225 | 1000×572×225 | 1200×572×225 | 1200×572×225 | 1500×572×225 | 1500×572×225 | 1500×572×225
| Net Weight | kg | 22.5(22.5) | 22.5(22.5) | 26(26) | 26(26) | 32.5(32.5) | 32.5(35) | 39(36.6) | 39(39) | 39(39)
| Packing Size (W×H×D) | mm | 889×683×312 | 889×683×312 | 1089×683×312 | 1089×683×312 | 1289×683×312 | 1289×683×312 | 1589×683×312 | 1589×683×312 | 1589×683×312
| Gross Weight | kg | 26.5(26.5) | 26.5(26.5) | 31(31) | 31(31) | 38(38) | 38(40) | 45(42.6) | 45(45) | 45(45)
Pipe Connection | Water-inlet pipe | inch | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4"
| Water-outlet pipe | inch | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4" | G3/4"
| Drain pipe | mm | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16
Note:
1.The data is the performance in high speed with relevant static pressure.
2.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB,19°C WB.
Heating Conditions: Entering Water 50°C, enter air temperature 20°C, the same water flow as the cooling conditions.
3.Noise is tested in full-anechoic test room.

## DS
Model MKD- |  |  | 300S | 400S | 500S
Air Volume | High | m3/h | 510 | 680 | 850
|  | CFM | 300 | 400 | 500
| Med | m3/h | 440 | 580 | 730
|  | CFM | 260 | 340 | 430
| Low | m3/h | 360 | 480 | 600
|  | CFM | 210 | 280 | 350
Cooling Capacity |  | W | 2500 | 2900 | 3500
Heating Capacity |  | W | 3700 | 4600 | 5100
Power Input |  | W | 50 | 70 | 95
Noise(Hi/Med/Lo) |  | dB(A) | 36/33/28 | 42/39/32 | 45/42/34
Water Flow | Cooling | L/min | 7.2 | 8.4 | 10
| Heating | L/min | 5.3 | 6.6 | 7.3
Water Pressure Drop | Cooling | kPa | 22 | 16 | 24
| Heating | kPa | 17 | 23 | 27
Fan Motor | Type | \ | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Model | \ | YDK15-6P | YDK37-4P | YDK37-4P
| Capacitor | uF | 1.5 | 2 | 2.5
| Quantity | \ | 1 | 1 | 1
Fan | Type | \ | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity | \ | 1 | 1 | 1
Coil | Row | \ | 2 | 2 | 2
| Tube pitch(a) x row pitch(b) | mm | 21×13.37 | 21×13.37 | 21×13.37
| Fin spacing | mm | 1.3 | 1.3 | 1.3
| Fin type | \ | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium
| Tube outside dia. | mm | Φ7 | Φ7 | Φ7
| Coil length x height | \ | 1315×210 | 1315×210 | 1315×210
| Number of circuits | \ | 3 for cold water | 4 for cold water | 4 for cold water
|  |  | 3 for hot water | 3 for hot water | 3 for hot water
| Max. Working Pressure | MPa | 1.6 | 1.6 | 1.6
Panel | Net Dimension (W×H×D) | mm | 647×50×647 | 647×50×647 | 647×50×647
| Net Weight | kg | 3 | 3 | 3
| Packing Size (W×H×D) | mm | 715×123×715 | 715×123×715 | 715×123×715
| Gross Weight | kg | 5 | 5 | 5
Indoor Unit | Net Dimension (W×H×D) | mm | 575×261×575 | 575×261×575 | 575×261×575
| Net Weight | kg | 17.5 | 17.5 | 17.5
| Packing Size (W×H×D) | mm | 670×290×670 | 670×290×670 | 670×290×670
| Gross Weight | kg | 21.5 | 21.5 | 21.5
Pipe Connection | Water-inlet pipe | inch | Cold water: G3/4" Hot water: G1/2" | Cold water: G3/4" Hot water: G1/2" | Cold water: G3/4" Hot water: G1/2"
| Water-outlet pipe | inch | Cold water: G3/4" Hot water: G1/2" | Cold water: G3/4" Hot water: G1/2" | Cold water: G3/4" Hot water: G1/2"
| Drain pipe | mm | ODΦ25 | ODΦ25 | ODΦ25
Controller |  | \ | R51/E (standard) | R51/E (standard) | R51/E (standard)
Note:
1.The data is the performance in high speed.
2.Cooling Conditions: Entering Water 7°C, Temperature Rise 5°C, Entering Air Temperature 27°C DB,19°CWB.
Heating Conditions: Entering Water 70°C, Entering/Leaving temperature difference is 10°C,enter air temperature 20°C.
3.Noise level is tested in semi-anechoic room.

## T3F
Model MKT3- |  |  |  | 200FG12 | 300FG12 | 400FG12 | 500FG12 | 600FG12 | 800FG12 | 1000FG12 | 1200FG12 | 1400FG12
|  |  |  | 200FG30 | 300FG30 | 400FG30 | 500FG30 | 600FG30 | 800FG30 | 1000FG30 | 1200FG30 | 1400FG30
Air flow |  | H/M/L | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020 | 2380/1785/1190
|  | H/M/L | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600 | 1400/1050/700
External Static pressure |  |  | Pa | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30 | G12 models: 12; G30 models: 30
Cooling | Capacity | H/M/L | kW | 2/1.76/1.52 | 2.7/2.35/2.13 | 3.6/3.15/2.76 | 4.3/3.74/3.32 | 5/4.32/3.84 | 6.8/5.78/5.11 | 7.8/6.74/5.88 | 10.2/8.89/7.85 | 11.5/9.9/8.86
| Water flow rate | H | L/h | 344 | 464 | 619 | 740 | 860 | 1170 | 1342 | 1754 | 1978
| Water pressure drop | H | kPa | 7.6 | 14.4 | 8.2 | 9.5 | 17.2 | 18.8 | 30 | 40.3 | 51.9
Heating | Capacity | H/M/L | kW | 3/2.64/2.22 | 4/3.48/3 | 5.2/4.47/3.9 | 5.7/5.02/4.33 | 7.2/6.19/5.33 | 9.6/8.45/7.2 | 10.8/9.61/8.1 | 13.5/12.15/10.26 | 15.5/13.48/11.78
| Water flow rate | H | L/h | 258 | 344 | 447 | 490 | 619 | 826 | 929 | 1161 | 1333
| Water pressure drop | H | kPa | 6.8 | 12.5 | 23.5 | 24 | 40.7 | 20.7 | 34.7 | 28.6 | 55.2
Power supply |  |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Power input | 12Pa | H | W | 33 | 53 | 66 | 87 | 100 | 145 | 180 | 210 | 222
| 30Pa | H | W | 49 | 64 | 75 | 96 | 114 | 154 | 193 | 230 | 278
Sound pressure level | 12Pa | H/M/L | dB(A) | 35/32/26 | 36/33/27 | 37/34/28 | 40/36/30 | 42/38/32 | 43/39/33 | 45/41/35 | 46/42/36 | 48/44/38
| 30Pa | H/M/L | dB(A) | 41/37/31 | 42/38/32 | 43/39/33 | 44/40/34 | 45/41/35 | 46/42/36 | 47/43/37 | 48/44/38 | 49/45/39
Fan motor | Type |  |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2
Fan | Type |  |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4
Coil | Row |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Max. working pressure |  | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter |  | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body | Dimensions | W×H×D | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522 | 2022×241×522
| Packing | W×H×D | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550 | 2070×260×550
| Net weight |  | kg | 15.1 | 17.5 | 20.7 | 20.7 | 23.5 | 32.4 | 34.9 | 40 | 43.6
| Gross weight |  | kg | 17.4 | 20 | 23.1 | 23.1 | 26.5 | 36 | 38.6 | 43.5 | 48.9
Pipe connection | Water inlet/outlet pipe |  | inch | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4 | Cold water: RC3/4 Hot water: RC3/4
| Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note:
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.The data is based on 12Pa external static pressure for G12 models, 30Pa for G30 models.
3.Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB,19°C WB.
Heating conditions: entering water 70°C, entering/leaving temperature difference is 10°C, enter air temperature 20°C.
4.Noise is tested in semi-anechoic test room.

## S4
Model MKS4 - |  |  | 200G30 | 300G30 | 400G30 | 500G30 | 600G30 | 800G50-A4 | 1000G50-A4 | 12000G50-A4 | 1400G50-A4 | 1600G50-A4 | 18000G50-A4 | 2000G50-A4
Power supply |  | V/Ph/Hz | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50 | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 430/380/340 | 600/540/480 | 700/630/520 | 900/810/720 | 1160/1040/930 | 1400/1342/1200 | 1650/1527/1405 | 2040/1851/1666 | 2420/1850/1657 | 2580/2320/2060 | 3380/2239/1878 | 3660/2544/2199
|  | CFM | 253/224/200 | 353/318/282 | 412/370/305 | 530/476/424 | 682/612/547 | 824/789/705 | 970/898/826 | 1200/1089/980 | 1424/1088/975 | 1518/1365/1212 | 1988/1317/1105 | 2153/1496/1295
Standard external static pressure |  | Pa | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Cooling | Capacity (H/M/L) | kW | 2.05/1.742/1.55 | 2.61/2.21/1.98 | 4.03/3.42/3.06 | 4.57/3.88/3.47 | 6.39/5.43/4.85 | 6.93/5.89/5.26 | 7.57/6.43/5.75 | 10.11/8.59/7.68 | 11.5/9.7/8.74 | 11.74/9.97/8.92 | 14.74/12.52/11.2 | 16.1/13.68/12.23
| Water flow rate | L/h | 196 | 249 | 385 | 437 | 610.6 | 662 | 723 | 966 | 1099 | 1122 | 1408 | 1538
| Water pressure drop | kPa | 10 | 10 | 21 | 25 | 53.8 | 13.3 | 16.3 | 21 | 25.3 | 27.8 | 37.9 | 48.1
Power input |  | W | 47/38/33 | 65/52/46 | 78/62/55 | 92/74/64 | 116/93/81 | 144/115/101 | 176/141/123 | 320/256/224 | 392/314/274 | 482/386/337 | 538/430/376 | 583/466/408
Sound pressure level |  | dB(A) | 38/33/27 | 39/34/28 | 39/35/29 | 41/35/30 | 42/36/31 | 48/47/46 | 49/48/47 | 51/50/48 | 52/50/49 | 53/51/50 | 54/51/50 | 54/52/51
Fan motor | Type |  | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor | Low noise 4-speed fan motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3
Coil | Row |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Net dimensions (W×H×D) |  | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1180x340x612 | 1180x340x612 | 1369x340x612 | 1369x340x612 | 1369x340x612 | 1500x340x612 | 1500x340x612
Packing size (W×H×D) |  | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1310x380x693 | 1310x380x693 | 1490x380x693 | 1490x380x693 | 1490x380x693 | 1620x380x693 | 1620x380x693
Net weight |  | kg | 15.3 | 17.5 | 20.7 | 20.7 | 23.5 | 39.3 | 40.8 | 46.3 | 46.3 | 46.3 | 54.8 | 54.8
Gross weight |  | kg | 17.6 | 20 | 23.1 | 23.1 | 26.5 | 47 | 49.6 | 56.4 | 56.4 | 56.4 | 64.6 | 64.6
Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
Drain pipe |  | mm | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24 | ODΦ24
Note:
1.H: high fan speed; M: medium fan speed; L: low fan speed.
2.The data is the performance in relevant standard external static pressure.
3.Cooling conditions: Entering water 5.5°C, Leaving water 14.5°C, Entering air temperature 27°C DB / 19°C WB.
4.Noise is tested in a semi-anechoic test room.