## MA
code |  |  | 22022010006152 | 22022010006153 | 22022010006154 | 22022010006155
Indoor code |  |  | 22022011006578 | 22022011006579 | 22022011006580 | 22022011006581
outdoor code |  |  | 22022016007319 | 22022016007320 | 22022016005282 | 22022016007321
Model |  |  | MSMAAU-09HRDN1-QRD0GW | MSMABU-12HRDN1-QRD0GW | MSMACU-18HRFN1-QRD0GW | MSMADU-24HRFN1-QRD0GW
Indoor |  |  | MSMAAU-09HRDN1-QRD0GW | MSMABU-12HRDN1-QRD0GW | MSMACU-18HRFN1-QRD0GW | MSMADU-24HRFN1-QRD0GW
Outdoor |  |  | MOBA03-09HFN1-QRD0GW | MOBA03-12HFN1-QRD0GW | MOB02-18HFN1-QRD0GW | MOCA02-24HFN1-QRD0GW
Power supply |  | Ph-V-Hz | 220-240V~ 50Hz, 1Ph | 220-240V~ 50Hz, 1Ph | 220-240V~ 50Hz, 1Ph | 220-240V~ 50Hz, 1Ph
Rated Cooling | Capacity | Btu/h | 9000(3500-11000) | 12000(3700-14000) | 18000(6200~20900) | 24000（9100-26900）
Cooling Power input |  | W | 821(100-1240) | 1256(100-1580) | 1643(140~2360) | 2502(240-3030)
Cooling Current |  | A | 3.6(0.4-5.4) | 5.5(0.4-6.9) | 7.1(0.6~10.3) | 10.8(1.0-13.2)
Rated Heating | Capacity | Btu/h | 10000(2800-11500) | 13000(3000-14400) | 19000(4700~23000) | 25000（5500-30000）
Heating Power input |  | W | 811(120-1200) | 1186(130-1510) | 1633(200~2410) | 2282(260-3140)
Heating Current |  | A | 3.5(0.5-5.2) | 5.2(0.6-6.6) | 7.1(0.9~10.5) | 9.9(1.1-13.7)
Seasonal Cooling | Pdesignc | kW | 2.6 | 3.5 | 5.3 | 7.03
| SEER | W/W | 6.1 | 6.1 | 6.7 | 6.1
| Energy Efficiency Class |  | A++ | A++ | A++ | A++
Heating(Average ) | Pdesignh | kW | 2.2 | 2.4 | 4.4 | 5.4
| SCOP | W/W | 4 | 4 | 4.1 | 4
| Energy Efficiency Class |  | A+ | A+ | A+ | A+
| Tbiv | ℃ | -7 | -7 | -7 | -10
Heating(Warmer ) | Pdesignh | kW | 2.8 | 2.9 | 4.4 | 6.3
| SCOP | W/W | 4.6 | 4.8 | 5.3 | 5.1
| Energy Efficiency Class |  | A++ | A++ | A+++ | A+++
| Tbiv | ℃ | 2 | 2 | 2 | 2
Tol |  | ℃ | -15 | -15 | -15 | -15
Moisture Removal |  | L/h | / | / | / | /
Max. input consumption |  | W | 2075 | 2200 | 2550 | 3700
Max. current |  | A | 9.5 | 10 | 11.5 | 17
Starting current |  | A | ---- | ---- | ---- | ----
Compressor | Model |  | ASK89D53UEZ | ASK89D53UEZ | ASM135D23UFZ | ATF235D22UMT
| Type |  | ROTARY | ROTARY | ROTARY | ROTARY
| Brand |  | GMCC | GMCC | GMCC | GMCC
| Capacity | Btu/h | 9010 | 9010 | 13836 | 24345
| Input | W | 671 | 671 | 1035 | 1970
| Rated current(RLA) | A | 2.2 | 2.2 | 7.32 | 6.95
| Locked rotor Amp(LRA) | A | 3.5 | 3.5 | ---- | ----
| Thermal protector |  | ---- | ---- | ---- | ----
| Thermal protector position |  | ---- | ---- | ---- | ----
| Capacitor | uF | ---- | ---- | ---- | ----
| Refrigerant oil/oil charge | ml | SUNISO 4GSD/NM56EP 280 ml | SUNISO 4GSD/NM56EP 280 ml | VG74/450 | POE(VG74)/670
Indoor fan motor | Model |  | YKFG-13-4-38L | YKFG-13-4-38L | ZKFP-30-8-3 | ZKFP-58-8-1
| Output | W | 45(Input) | 45(Input) | 30 | 58
| Capacitor | uF | 1.5 | 1.5 | - - | - -
| Speed(Hi/Mi/Lo) | r/min | 1130 / 900 /750 | 1130 / 900 / 800 | 1150 / 1000 / 850 | 1150/1000/780
Indoor coil | a.Number of rows |  | 2 | 2 | 2 | 2
| b.Tube pitch(a)x row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37 | 21x13.37
| c.Fin spacing | mm | 1.3 | 1.2 | 1.2 | 1.3
| d.Fin type (code) |  | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium
| e.Tube outside dia.and type | mm | Φ7,innergroove tube | Φ5,innergroove tube | Φ7,innergroove tube | Φ7, innergroove tube
| f.Coil length x height x width | mm | 510x84x13.37+510x189x26.74 | 595x84x19.5+595x210x19.5 | 750x294x26.74 | 780x336x26.74
| g.Number of circuits |  | 2 | 3 | 3 | 4
Indoor air flow (Hi/Mi/Lo) |  | m3/h | 490/370/270 | 600/480/380 | 860/690/460 | 1000/850650
Indoor sound pressure level (Hi/Mi/Lo) |  | dB(A) | 39/33/29 | 41.5/ 36/28.5 | 44.5/39/32.5 | 46.5/40/34
Indoor sound power level (Hi) |  | dB(A) | 53 | 53 | 57 | 60
Indoor unit | Dimension(W*D*H) | mm | 715x205x285 | 805x205x285 | 958x213x302 | 1038x220x325
| Packing (W*D*H) | mm | 780x285x360 | 870x285x360 | 1035x305x380 | 1120x405x330
| Net/Gross weight | Kg | 6.5/8.5 | 7.5/9.5 | 8.5/12 | 12/15
Outdoor fan motor | Model |  | ZKFN-40-8-1L | ZKFN-40-8-1L | ZKFN-40-8-1L | ZKFN-50-8-2
| Output | W | 40 | 40 | 40 | 50
| Capacitor | uF | - - | - - | - - | - -
| Speed | r/min | 810/710/520 | 810/710/520 | 810/700/550 | 810/750/600
Outdoor coil | a.Number of rows |  | 1 | 1 | 2 | 2
| b.Tube pitch(a)x row pitch(b) | mm | 21x13.37 | 21x13.37 | 25.4x22 | 25.4x22
| c.Fin spacing | mm | 1.4 | 1.4 | 1.4 | 1.4
| d.Fin type (code) |  | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium
| e.Tube outside dia.and type | mm | Φ7,innergroove tube | Φ7,innergroove tube | Φ9.52,innergroove tube | Φ9,innergroove tube
| f.Coil length x height x width | mm | 755x504x13.37 | 755x504x13.37 | 860x508x44 | 730x660.4x44
| g.Number of circuits |  | 2 | 2 | 4 | 4
Outdoor air flow |  | m3/h | 1800 | 1800 | 2100 | 2700
Outdoor sound pressure level |  | dB(A) | 55 | 56 | 57 | 60
Outdoor sound power level |  | dB(A) | 60 | 60 | 63 | 65
Outdoor unit | Dimension(W*D*H) | mm | 770x300x555 | 770x300x555 | 800x333x554 | 845x363x702
| Packing (W*D*H) | mm | 900x348x615 | 900x348x615 | 920x390x615 | 965x395x755
| Net/Gross weight | Kg | 25.2/27.4 | 25.5/27.7 | 37.8/40.5 | 48.4/51.6
Refrigerant | Type |  | R410A | R410A | R410A | R410A
| GWP |  | 2088 | 2088 | 2088 | 2088
| Charged quantity | Kg | 0.8 | 0.8 | 1.48 | 1.85
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5 | 4.2/1.5
Refrigerant piping | Liquid side/ Gas side | mm(inch) | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ12.7(1/4"/1/2") | Φ9.52/Φ15.9(3/8"/5/8")
| Max. refrigerant pipe length | m | 25 | 25 | 30 | 50
| Max. difference in level | m | 10 | 10 | 20 | 25
Connection wiring |  |  | 1.5(Optional) | 1.5(Optional) | 1.5(Optional) | 2.5(Optional)
Plug type |  |  | -- | -- | -- | --
Thermostat type |  |  | Remote Control | Remote Control | Remote Control | Remote Control
Operation temperature | Indoor(cooling/ heating) | ℃ | 17～32/0～30 | 17～32/0～30 | 17～32/0～30 | 17～32/0～30
| Outdoor(cooling/heating) | ℃ | -15～50/-15～30 | -15～50/-15～30 | -15～50/-15～30 | -15～50/-15～30
Application area | minimum | m2 | 12 | 15.9864 | 24 | 32
| maximum | m2 | 18 | 23.4467 | 35 | 47
Qty’per 20’ /40’ /40'HQ |  |  | 114/236/260 | 108/224/250 | 82/170/192 | 66/135/152