## Small Cassette
|  |  | PD22315033 | PD22315033 | PD22315033
Code |  |  | 22022311000291 | 22022511002476 | 22022511002478
Model |  |  | MCA3I-09HRFN8-QRD0 | MCA3U-12HRFN8-QRD0W | MCA3U-18HRFN8-QRC8W
Power supply |  | V,Hz,Ph | 220-240-1-50 | 220-240-1-50 | 220-240-1-50
Cooling | Capacity | Btu/h | 9000 | 12000 | 18000
| Input | W | 40 | 40 | 102
| Rated current | A | 0.18 | 0.18 | 0.44
Heating | Capacity | Btu/h | 10000 | 13000 | 19000
| Input | W | 40 | 40 | 102
| Rated current | A | 0.18 | 0.18 | 0.44
Indoor fan motor | Model |  | ZKFP-46-8-1 | ZKFP-46-8-1 | ZKFP-46-8-1
| Old Model |  | WZDK46-38G | WZDK46-38G | WZDK46-38G
| Qty |  | 1 | 1 | 1
| Input | w | 45 | 45 | 46(Output)
| Capacitor | uF | / | / | /
| Speed(hi/mi/lo) | r/min | 600/520/460 | 600/520/460 | 730/630/570
Indoor coil | a.Number of rows |  | 1 | 1 | 2
| b.Tube pitch(a)x row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37
| c.Fin spacing | mm | 1.3 | 1.3 | 1.3
| d.Fin type (code) |  | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium
| e.Tube outside dia.and type | mm | Φ7,innergroove tube | Φ7,innergroove tube | Φ7,innergroove tube
| f.Coil length x height x width | mm | 1380x210x13.37 | 1380x210x13.37 | 1360x210x26.74
| g.Number of circuits |  | 2 | 2 | 4
Indoor air flow |  | m3/h | 580/500/450 | 650/530/450 | 680/560/500
Indoor sound pressure level |  | dB(A) | 38/33/29 | 42/38/34 | 44/42/41
Indoor sound power level |  | dB(A) | 53 | 56 | 56
Indoor unit | Dimension (W x Dx H)(body) | mm | 570x570x260 | 570x570x260 | 570x570x260
| Packing (W x Dx H)(body) | mm | 662x662x317 | 662x662x317 | 655x655x290
| Dimension (W x Dx H)(panel) | mm | 647x647x50 | 647x647x50 | 647x647x50
| Packing (W x Dx H)(panel) | mm | 715x715x123 | 715x715x123 | 715x715x123
| Net/Gross weight(body) | kg | 14.7/19.3 | 14.4/17.2 | 16.1/18.9
| Net/Gross weight | kg | 2.5/4.5 | 2.5/4.5 | 2.5/4.5
Design pressure |  | MPa | 4.6/1.7 | 4.6/1.7 | 4.6/1.7
Drainage water pipe dia. |  | mm | ODΦ25 | ODΦ25 | ODΦ25
Refrigerant piping | Liquid side/ Gas side | mm | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ12.7(1/4"/1/2")
Controller |  |  | Remote control | Remote control | Remote control
Room temperature | Cooling | ℃ | 17-32 | 17-32 | 17-32
| Heating | ℃ | 0-30 | 0-30 | 0-30
Operation temperature |  | ℃ | 17-30 | 17-30 | 17-30

## Outdoor
|  |  | PD22315033 |  | PD22315032 |  |  | PD22316008 |  |  |  | PD22316009
Outdoor Code |  |  | 22022316000765 |  | 22022316000745 |  |  | 22022316000845 |  |  |  | 22022316000887
Outdoor Model |  |  | M2OC-18HFN8-Q |  | M3OE-27HFN8-Q |  |  | M4OB-36HFN8-Q |  |  |  | M5OD-42HFN8-Q
Indoor unit combination |  |  | Range | MCA3I-09HRFN8-QRD0 | Single | Double | MCA3I-09HRFN8-QRD0 | Single | Double | Three | MCA3I-09HRFN8-QRD0 | Single | Double | Three | FOUR | MCA3I-09HRFN8-QRD0
Power supply |  | V,Hz,Ph | 220-240V- 50Hz, 1Ph |  | 220-240V- 50Hz, 1Ph |  |  | 220-240V- 50Hz, 1Ph |  |  |  | 220-240V,50Hz, 1Ph
Cooling | Capacity | Btu/h | 7000-18000 | 18000 | 7000-18000 | 14000-27000 | 27000 | 7000-18000 | 14000-26000 | 21000-36000 | 36000 | 7000-18000 | 14000-28000 | 21000-36000 | 28000-40000 | 42000
| Input | W | 690-2000 | 1800 | 750-1700 | 1400-2470 | 2470 | 1250-1700 | 1650-2320 | 2150-3520 | 3600 | 680-1800 | 1400-2780 | 2100-3450 | 2700-3700 | 3830
| Rated current | A | 3.13-9.27 | 7.8 | 3.3-7.4 | 6.1-10.7 | 10.7 | 5.4-7.4 | 7.2-10.1 | 9.3-15.3 | 16.48 | 3.0-8.0 | 6.2-11.8 | 9.0-15.0 | 11.6-16.0 | 17.4
| EER | W/W | / | 3.01 | / | / | 3.22 | / | / | / | 2.93 | / | / | / | / | 3.21
Heating | Capacity | Btu/h | 8000-19000 | 19000 | 8000-20000 | 16000-28000 | 28000 | 8000-20000 | 16000-29000 | 24000-38000 | 36000 | 8000-20000 | 14000-28000 | 21000-36000 | 28000-40000 | 42000
| Input | W | 600-1670 | 1550 | 720-1750 | 1520-2350 | 2350 | 1375-2440 | 2050-3340 | 2880-3360 | 3000 | 680-1800 | 1400-2680 | 1995-3330 | 2580-3570 | 3400
| Rated current | A | 2.81-7.74 | 6.7 | 3.2-7.7 | 6.6-10.2 | 10.2 | 5.9-10.6 | 8.9-14.5 | 12.5-14.6 | 13.73 | 3.0-8.0 | 6.2-11.3 | 8.5-14.5 | 11.1-15.8 | 15.5
| COP | W/W | / | 3.59 | / | / | 3.49 | / | / | / | 3.52 | / | / | / | / | 3.62
Seasonal Cooling | Pdesignc | kW | 5.2 |  | 7.9 |  |  | 10.5 |  |  |  | 12.3
| SEER | W/W | 5.8 |  | 6.2 |  |  | 6.1 |  |  |  | 5.8
| Energy Efficiency Class |  | A+ |  | A++ |  |  | A++ |  |  |  | A+
Heating(Average ) | Pdesignh | kW | 4.5 |  | 5.2 |  |  | 8.4 |  |  |  | 9.4
| SCOP | W/W | 3.8 |  | 4.0 |  |  | 4 |  |  |  | 3.8
| Energy Efficiency Class |  | A |  | A+ |  |  | A+ |  |  |  | A
| Tbiv | ℃ | -7 |  | -7 |  |  | -7 |  |  |  | -7
Heating(Warmer ) | Pdesignh |  | 5.0 |  | 6.3 |  |  | 9.3 |  |  |  | 10.1
| SCOP |  | 5.3 |  | 5.2 |  |  | 5.4 |  |  |  | 5.2
| Energy Efficiency Class |  | A+ |  | A+++ |  |  | A+++ |  |  |  | A+++
| Tbiv | ℃ | 2 |  | 2 |  |  | 2 |  |  |  | 2
Tol |  | ℃ | -15 |  | -15 |  |  | -15 |  |  |  | -15
Max. input consumption |  | W | 2300 |  | 3100 |  |  | 4600 |  |  |  | 4700
Max. input current |  | A | 12 |  | 15 |  |  | 21.5 |  |  |  | 22
Compressor | Model |  | KSM135D23UFZ |  | KTF235D22UMT |  |  | KTF310D43UMT |  |  |  | KTF310D43UMT
| Type |  | ROTARY |  | ROTARY |  |  | ROTARY |  |  |  | ROTARY
| Brand |  | GMCC |  | GMCC |  |  | GMCC |  |  |  | GMCC
| Capacity | Btu/h | 14433 |  | 26100 |  |  | 10010W |  |  |  | 10010W
| Input | W | 1080 |  | 2065 |  |  | 2765 |  |  |  | 2765
| Rated current(RLA) | A | 7.10 |  | 9.4 |  |  | 5.38 |  |  |  | 5.38
| Locked rotor Amp(LRA) | A | ---- |  | ---- |  |  | ---- |  |  |  | -----
| Thermal protector position |  | ---- |  | ---- |  |  | ---- |  |  |  | -----
| Capacitor | μF | ---- |  | ---- |  |  | ---- |  |  |  | -----
| Refrigerant oil | ml | VG74 /450 |  | ESTEL OIL RB74AF/670 |  |  | VG74/1000 |  |  |  | VG74/1000
Outdoor fan motor | New Model |  | ZKFN-40-8-1L |  | ZKFN-50-8-2 |  |  | ZKFN-120-8-2 |  |  |  | ZKFN-120-8-2
| Model | [6 empty] | WZDK120-38G-W |  |  |  | WZDK120-38G-W
| Qty |  | 1 |  | 1 |  |  | 1 |  |  |  | 1
| Output | W | 63 |  | 115 |  |  | 150 |  |  |  | 150
| Capacitor | μF | ----- |  | ----- |  |  | ----- |  |  |  | -----
| Speed(Hi/Med/Lo) | r/min | 850/750/650 |  | 850/750/600 |  |  | 900/750/600 |  |  |  | 900/750/600
Outdoor coil | Number of rows |  | 2 |  | 2 |  |  | 2 |  |  |  | 2
| Tube pitch(a)* row pitch(b) | mm | 25.4x22 |  | 25.4x22 |  |  | 25.4x22 |  |  |  | 25.4x22
| Fin spacing | mm | 1.4 |  | 1.4 |  |  | 1.3 |  |  |  | 1.3
| Fin type |  | Hydrophilic aluminium |  | Hydrophilic aluminium |  |  | Hydrophilic aluminium |  |  |  | Hydrophilic aluminium
| Tube outside dia.and type | mm | Φ9,innergroove tube |  | Φ9.52,innergroove tube |  |  | Ф9.52, innergroove tube |  |  |  | Ф9.52, innergroove tube
| Coil length * height * width | mm | 860x508x44 |  | 730x660.4x44 |  |  | 995x762x44 |  |  |  | 978x762x44+580x762x22
| Number of circuits |  | 4 |  | 4 |  |  | 4 |  |  |  | 4
Outdoor air flow |  | m3/h | 2200 |  | 2700 |  |  | 4000 |  |  |  | 3850
Indoor sound power level |  | dB(A) | 53 |  | 53 |  |  | 53 |  |  |  | 53
Outdoor sound pressure level |  | dB(A) | 56 |  | 59 |  |  | 63 |  |  |  | 62
Outdoor sound power level |  | dB(A) | 63 |  | 65 |  |  | 68 |  |  |  | 71
Throttle type |  |  | Capillary+EXV |  | Capillary+EXV |  |  | Capillary+EXV |  |  |  | Capillary+EXV
Outdoor unit | Dimension(WxDxH) | mm | 800x333x554 |  | 845x363x702 |  |  | 946x410x810 |  |  |  | 946x410x810
| Packing(WxDxH) | mm | 920x390x615 |  | 965x395x765 |  |  | 1090x500x875 |  |  |  | 1090x500x875
| Net/Gross weight | kg | 36/39 |  | 53/56.5 |  |  | 68.8/75.6 |  |  |  | 73.3/80.4
Refrigerant | Type |  | R32 |  | R32 |  |  | R32 |  |  |  | R32
| GWP |  | 675 |  | 675 |  |  | 675 |  |  |  | 675
| Charged quantity | Kg | 1.3 |  | 1.57 |  |  | 2.1 |  |  |  | 2.4
Design pressure |  | MPa | 4.6/1.7 |  | 4.6/1.7 |  |  | 4.6/1.7 |  |  |  | 4.6/1.7
Refrigerant piping | Liquid side/ Gas side | mm(inch) | 2 x Φ6.35/Φ9.52(1/4"/3/8") |  | 3 x Φ6.35/Φ9.52(1/4"/3/8") |  |  | 4 x Φ6.35/3x Φ9.52+1xΦ12.7(4x1/4"/3x3/8"+1x1/2") |  |  |  | 5 x Φ6.35/4x Φ9.52+1xΦ12.7(5x1/4"/4x3/8"+1x1/2")
| Max. length for all rooms | m | 40 |  | 60 |  |  | 80 |  |  |  | 80
| Max. length for one indoor unit | m | 25 |  | 30 |  |  | 35 |  |  |  | 35
| Max. height difference between indoor and outdoor unit | m | 15 |  | 15 |  |  | 15 |  |  |  | 15
| Max. height difference between indoor units | m | 10 |  | 10 |  |  | 10 |  |  |  | 10
Ambient temperature | Cooling | ℃ | -15-50 |  | -15-50 |  |  | -15-50 |  |  |  | -15-50
| Heating | ℃ | -15-24 |  | -15-24 |  |  | -15-24 |  |  |  | -15-24
Remarks:
1.The above design and specifications are subject to change without prior notice for product improvement.
2.The values given in the table for the noise level reflect the levels in hemi-anechoic rooms.

## multi duct
Code |  |  | 22023011004102 | 22023011004322 | 22023011004321
Model |  |  | MTIU-12HWFNX-QRD0W | MTIU-07HWFNX-QRD0W | MTIU-09HWFNX-QRD0W
Power supply |  | V-ph-Hz | 220-240,50,1 | 220-240,50,1 | 220-240,50,1
Cooling | Capacity | Btu/h | 12000 | 7000 | 9000
| Input | W | 40 | 40 | 40
| Rated current | A | 0.17 | 0.17 | 0.17
Heating | Capacity | Btu/h | 13000 | 8000 | 10000
| Input | W | 40 | 40 | 40
| Rated current | A | 0.17 | 0.17 | 0.17
Indoor fan motor | Model |  | ZKFN-55-8-22 | ZKFN-55-8-22 | ZKFN-55-8-22
| Old Model |  | ZKFN-55-8-22 | ZKFN-55-8-22 | ZKFN-55-8-22
| Qty |  | 1 | 1 | 1
| Input | W | 130 | 130 | 130
| Capacitor | uF | --- | --- | ---
| Speed(Hi/Med/Lo) | r/min | 1170/1030/850 | 1170/1030/850 | 1170/1030/850
Indoor coil | Number of rows |  | 3 | 3 | 3
| Tube pitch(a)*row pitch(b) | mm | 21x13.37 | 21x13.37 | 21x13.37
| Fin spacing | mm | 1.4 | 1.4 | 1.4
| Fin type |  | Hydrophilic aluminium | Hydrophilic aluminium | Hydrophilic aluminium
| Tube outside dia.and type | mm | Ф7,innergroove tube | Ф7,innergroove tube | Ф7,innergroove tube
| Coil length * height * width | mm | 526x210x40.11 | 526x210x40.11 | 526x210x40.11
| Number of circuits |  | 4 | 4 | 4
Indoor air flow |  | m3/h | 600/480/300 | 500/340/230 | 500/340/230
ESP | Rated | Pa | 25 | 25 | 25
| Range | Pa | 0-60 | 0-40 | 0-40
Indoor sound pressure level |  | dB(A) | 42/38/35 | 42/38/35 | 42/38/35
Indoor sound power level |  | dB(A) | 59 | 59 | 59
Indoor unit | Dimension (WxDxH) | mm | 700x450x200 | 700x450x200 | 700x450x200
| Packing(WxDxH) | mm | 860x540x275 | 860x540x275 | 860x540x275
| Net/Gross weight | kg | 18/22 | 18/22 | 18/22
Design pressure |  | MPa | 4.2/1.5 | 4.2/1.5 | 4.2/1.5
Drainage water pipe diameter |  | mm | ODΦ25 | ODΦ25 | ODΦ25
Refrigerant piping | Liquid side/ Gas side | mm | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ9.52(1/4"/3/8") | Φ6.35/Φ9.52(1/4"/3/8")
Controller |  |  | Wired control | Wired control | Wired control
Room temperature | Cooling | ℃ | 17-32 | 17-32 | 17-32
| Heating | ℃ | 0-30 | 0-30 | 0-30
Operation temperature |  | ℃ | 17-30 | 17-30 | 17-30