## A
Model |  |  | MKA-V600R | MKA-V750R | MKA-V850R | MKA-V950R | MKA-V1200R | MKA-V1500R
Power supply |  | V/Ph/Hz | 220-240/1/50 |  |  | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 1133/793/567 | 1255/879/628 | 1441/1009/721 | 1494/1046/747 | 1596/1117/798 | 1850/1295/925
|  | CFM | 667/467/334 | 739/517/370 | 848/594/424 | 879/616/440 | 940/657/470 | 1089/762/544
Cooling | Capacity (H/M/L) | kW | 5.58/4.35/3.52 | 5.77/4.5/3.63 | 6.84/5.33/4.3 | 6.99/5.27/4.16 | 7.01/5.32/4.34 | 10.64/8.09/6.6
| Water flow rate | L/h | 960 | 992 | 1176 | 1202 | 1206 | 1830
| Water pressure drop | kPa | 21 | 28 | 27 | 25 | 23 | 36
Heating | Capacity (H/M/L) | kW | 7.72/5.92/4.5 | 8.15/6.12/4.65 | 9.37/7.25/5.5 | 9.52/7.35/5.32 | 9.62/7.43/5.55 | 14.38/11.29/8.44
| Water pressure drop | kPa | 22 | 26 | 23 | 20 | 20 | 34
Power input |  | W | 42 | 50 | 64 | 71 | 90 | 124
Sound pressure level (H/M/L) |  | dB(A) | 42/33/26 | 45/37/28 | 46/36/28 | 47/37/31 | 48/39/32 | 50/40/33
Fan motor | Type |  | DC motor | DC motor | DC motor | DC motor | DC motor | DC motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2 | 2 | 2 | 3
| Max. Working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
Panel | Net dimensions (W×H×D) | mm | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950
| Packing size (W×H×D) | mm | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035
| Net weight | kg | 6 | 6 | 6 | 6 | 6 | 6
| Gross weight | kg | 9 | 9 | 9 | 9 | 9 | 9
Body | Net dimensions (W×H×D) | mm | 840×230×840 | 840×230×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840
| Packing size (W×H×D) | mm | 900×260×900 | 900×260×900 | 900×330×900 | 900×330×900 | 900×330×900 | 900×330×900
| Net weight | kg | 23 | 23 | 27 | 27 | 27 | 29.5
| Gross weight | kg | 28 | 28 | 33 | 33 | 33 | 34.5
Pipe connections | Water inlet/outlet pipe | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
| Drain pipe | mm | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 3. Noise is tested in a semi-anechoic test room.

## D
Model |  |  | MKD-V300 | MKD-V400 | MKD-V500
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 560/392/280 | 717/502/359 | 785/550/393
|  | CFM | 330/231/165 | 422/296/211 | 462/324/231
Cooling | Capacity (H/M/L) | kW | 3.02/2.3/1.75 | 3.93/3.07/2.48 | 4.24/3.31/2.67
| Water flow rate | L/h | 519 | 676 | 729
| Water pressure drop | kPa | 7.4 | 12 | 9.4
Heating | Capacity (H/M/L) | kW | 4.1/3/2.22 | 5.34/4/3.15 | 5.77/4.33/3.4
| Water pressure drop | kPa | 8 | 10.6 | 9.4
Power input |  | W | 22.7 | 27 | 32
Sound pressure level (H/M/L) |  | dB(A) | 34/29/21 | 40/36/28 | 43/37/30
Fan motor | Type |  | DC motor | DC motor | DC motor
| Quantity |  | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7
Panel | Net dimensions (W×H×D) | mm | 647×50×647 | 647×50×647 | 647×50×647
| Packing size (W×H×D) | mm | 715×123×715 | 715×123×715 | 715×123×715
| Net weight | kg | 2.5 | 2.5 | 2.5
| Gross weight | kg | 4.5 | 4.5 | 4.5
Body | Net dimensions (W×H×D) | mm | 575×261×575 | 575×261×575 | 575×261×575
| Packing size (W×H×D) | mm | 670×290×670 | 670×290×670 | 670×290×670
| Net weight | kg | 16.5 | 16.5 | 16.5
| Gross weight | kg | 22.5 | 22.5 | 22.5
Pipe connections | Water inlet/outlet pipe | inch | G3/4 | G3/4 | G3/4
| Drain pipe | mm | ODΦ25 | ODΦ25 | ODΦ25
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 3. Noise is tested in a semi-anechoic test room.

## T2
Model |  |  | MKT2-V200 | MKT2-V300 | MKT2-V400 | MKT2-V500 | MKT2-V600 | MKT2-V800 | MKT2-V1000 | MKT2-V1200
Power supply |  | V/Ph/Hz | 220-240/1/50 |  |  | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020
|  | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600
Standard external static pressure |  | Pa | 12Pa (default); 30/50Pa can be set through dial switch on PCB |  |  | The factory default 12Pa,30/50Pa can adjust in the field
Cooling | Capacity (H/M/L) | kW | 2/1.74/1.52 | 2.7/2.31/2.03 | 3.6/3.11/2.66 | 4.4/3.74/3.25 | 5.5/4.58/4.09 | 7.5/6.33/5.68 | 8.9/7.61/6.41 | 10.8/9.13/7.93
| Water flow rate | L/h | 344 | 464 | 619 | 757 | 946 | 1290 | 1531 | 1858
| Water pressure drop | kPa | 6.1 | 11.4 | 20.4 | 20.1 | 13.9 | 12.4 | 21.4 | 28.1
Heating | Capacity (H/M/L) | kW | 3.2/2.75/2.37 | 4.3/3.74/3.23 | 5.4/4.64/4.05 | 6.8/5.78/5.07 | 8.1/6.77/5.92 | 11/9.48/8.25 | 13.5/11.72/10.03 | 16.5/14.05/12.24
| Water pressure drop | kPa | 5.6 | 9.7 | 17.7 | 18.9 | 11.6 | 10.6 | 18.4 | 22.8
Power input |  | W | 20 | 26 | 38 | 48 | 54 | 74 | 99 | 135
Sound pressure level | 12Pa (H/M/L) | dB(A) | 35/32/25 | 36/33/26 | 37/34/27 | 38/35/28 | 39/36/29 | 40/37/30 | 42/39/32 | 44/40/33
| 30Pa (H/M/L) | dB(A) | 40/36/29 | 41/37/30 | 42/38/31 | 43/39/32 | 44/40/33 | 45/41/34 | 46/42/34 | 47/43/34
| 50Pa (H/M/L) | dB(A) | 43/39/31 | 44/40/32 | 45/41/33 | 46/42/34 | 47/43/35 | 48/44/36 | 50/45/37 | 50/46/38
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4
Coil | Row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Net dimensions (W×H×D) |  | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522
Packing size (W×H×D) |  | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550
Net weight |  | kg | 16.5 | 18.5 | 20 | 20 | 22.2 | 31.4 | 32.5 | 37.5
Gross weight |  | kg | 19 | 21.4 | 23.2 | 23.2 | 26 | 35.8 | 37.2 | 42.8
Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
Drain pipe |  | inch | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Air flow rate at 0Pa ESP. 3. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 4. Noise is tested in a semi-anechoic test room.

## T3
Model |  |  | MKT3-V200 | MKT3-V300 | MKT3-V400 | MKT3-V500 | MKT3-V600 | MKT3-V800 | MKT3-V1000 | MKT3-V1200
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020
|  | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600
Standard external static pressure |  | Pa | 12Pa (default); 30/50Pa can be set through dial switch on PCB |  |  | The factory default 12Pa,30/50Pa can adjust in the field
Cooling | Capacity (H/M/L) | kW | 2.2/1.9/1.68 | 3.1/2.7/2.3 | 4/3.4/2.95 | 4.5/3.96/3.45 | 5.8/4.88/4.45 | 8.2/6.88/6.25 | 9/7.8/6.57 | 11/9.8/8.35
| Water flow rate | L/h | 378.4 | 533.2 | 688 | 774 | 997.6 | 1410.4 | 1548 | 1892
| Water pressure drop | kPa | 9.4 | 20.6 | 9.7 | 17.5 | 30.1 | 30.4 | 21.8 | 22.7
Heating | Capacity (H/M/L) | kW | 3.5/3.08/2.59 | 5.3/4.61/3.98 | 6.8/5.85/5.1 | 7.9/6.95/6 | 9.8/8.6/7.4 | 13.6/11.97/10.2 | 15.5/14.24/12 | 20.1/18.27/15.43
| Water pressure drop | kPa | 8.2 | 16.8 | 11.4 | 14.8 | 25 | 26.8 | 18.4 | 19.9
Power input |  | W | 16 | 21 | 28 | 40 | 45 | 60 | 90 | 110
Sound pressure level | 12Pa (H/M/L) | dB(A) | 36/32/26 | 37/33/26 | 37/34/27 | 38/35/28 | 39/36/29 | 41/37/30 | 42/39/32 | 44/40/33
| 30Pa (H/M/L) | dB(A) | 40/36/29 | 41/38/30 | 42/38/31 | 43/38/32 | 44/40/33 | 45/40/34 | 46/42/34 | 47/42/34
| 50Pa (H/M/L) | dB(A) | 42/39/31 | 43/40/32 | 45/41/33 | 45/42/34 | 47/43/35 | 47/44/36 | 50/45/37 | 50/45/38
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
Fan | Type |  | Centrifugal, forward-curved Blades |  |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4
Coil | Row |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Net dimensions (W×H×D) |  | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522
Packing size (W×H×D) |  | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550
Net weight |  | kg | 16.7 | 19 | 21 | 21 | 23.7 | 33 | 34.7 | 39.2
Gross weight |  | kg | 19.7 | 22 | 24 | 24 | 27.2 | 37.2 | 39.2 | 44.4
Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
Drain pipe |  | inch | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Air flow rate at 0Pa ESP. 3. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 4. Noise is tested in a semi-anechoic test room.

## T4
Model |  |  | MKT4-V200 | MKT4-V300 | MKT4-V400 | MKT4-V500 | MKT4-V600 | MKT4-V800 | MKT4-V1000 | MKT4-V1200
Power supply |  | V/Ph/Hz | 220-240/1/50 |  |  | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 340/255/170 | 510/385/255 | 680/510/340 | 850/640/425 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020
|  | CFM | 200/150/100 | 300/225/150 | 400/300/200 | 500/375/250 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600
Standard external static pressure |  | Pa | 12Pa (default); 30/50Pa can be set through dial switch on PCB |  |  | The factory default 12Pa,30/50Pa can adjust in the field
Cooling | Capacity (H/M/L) | kW | 2.5/2.16/1.87 | 3.3/2.85/2.47 | 4.4/3.72/3.22 | 4.8/4.18/3.64 | 6.2/5.38/4.65 | 8.8/7.43/6.57 | 9.5/8.18/7.06 | 11.8/9.82/8.74
| Water flow rate | L/h | 430 | 567.6 | 756.8 | 825.6 | 1066.4 | 1513.6 | 1634 | 2029.6
| Water pressure drop | kPa | 2 | 4.8 | 9.3 | 9.6 | 18.8 | 12.5 | 14.5 | 23.1
Heating | Capacity (H/M/L) | kW | 4.1/3.51/3.03 | 5.8/5.05/4.35 | 7.1/6.11/5.33 | 8.5/7.04/6.28 | 10.5/9.03/7.77 | 14.5/12.38/10.88 | 16.3/13.45/12.05 | 20.1/16.72/14.88
| Water pressure drop | kPa | 5.6 | 9.7 | 17.7 | 18.9 | 11.6 | 10.6 | 18.4 | 22.8
Power input |  | W | 20 | 26 | 38 | 48 | 54 | 74 | 99 | 135
Sound pressure level | 12Pa (H/M/L) | dB(A) | 37/33/27 | 37/33/26 | 38/35/27 | 38/35/28 | 39/36/29 | 41/37/30 | 42/39/32 | 44/40/33
| 30Pa (H/M/L) | dB(A) | 41/36/30 | 41/38/30 | 42/38/31 | 43/38/32 | 44/40/33 | 45/40/34 | 46/42/35 | 47/42/35
| 50Pa (H/M/L) | dB(A) | 43/39/31 | 43/40/32 | 45/42/33 | 46/42/34 | 47/43/35 | 47/44/36 | 50/45/37 | 50/45/38
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
Fan | Type |  | Centrifugal, forward-curved Blades |  |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4
Coil | Row |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Net dimensions (W×H×D) |  | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522
Packing size (W×H×D) |  | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550
Net weight |  | kg | 17.8 | 20 | 21.9 | 21.9 | 25 | 34.8 | 36.4 | 41.9
Gross weight |  | kg | 20.4 | 22.9 | 25.1 | 25.1 | 28.8 | 39.2 | 41.9 | 47.2
Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
Drain pipe |  | inch | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Air flow rate at 0Pa ESP. 3. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 4. Noise is tested in a semi-anechoic test room.

## G
Model |  |  | MKG-V250B | MKG-V300B | MKG-V400B | MKG-V500B | MKG-V600B
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 425/410/320 | 510/427/349 | 680/550/504 | 850/692/586 | 1020/820/670
|  | CFM | 250/241/188 | 300/251/205 | 400/324/297 | 500/407/345 | 600/483/394
Cooling | Capacity (H/M/L) | kW | 2.63/2.2/1.97 | 2.97/2.48/2.06 | 3.28/2.90/2.66 | 4.25/3.78/3.05 | 5.0/3.95/3.21
| Water flow rate | L/h | 452 | 511 | 564 | 731 | 860
| Water pressure drop | kPa | 23.1 | 33.6 | 42 | 34.9 | 36.3
Heating | Capacity (H/M/L) | kW | 3.36/2.85/2.35 | 3.91/2.92/2.49 | 4.37/3.77/3.35 | 5.81/4.14/3.63 | 6.7/5.17/4.18
| Water pressure drop | kPa | 22 | 31.4 | 40 | 29.7 | 32.8
Power input |  | W | 10.7 | 14.3 | 33 | 28 | 37.5
Sound pressure level (H/M/L) |  | dB(A) | 30/26/23 | 32/28/25 | 36/32/29 | 38/34/30 | 40/36/31
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Tangential fan | Tangential fan | Tangential fan | Tangential fan | Tangential fan
| Quantity |  | 1 | 1 | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
Net dimensions (W×H×D) |  | mm | 915×290×230 | 915×290×230 | 915×290×230 | 1072×315×230 | 1072×315×230
Packing size (W×H×D) |  | mm | 1020×390×315 | 1020×390×315 | 1020×390×315 | 1180×415×315 | 1180×415×315
Net weight |  | kg | 12.7 | 12.7 | 12.7 | 15.1 | 14.9
Gross weight |  | kg | 17.3 | 17.6 | 16.3 | 19 | 18.6
Water inlet/outlet pipe |  | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4
Drain pipe |  | mm | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 3. Noise is tested in a semi-anechoic test room.
Model |  |  | MKG-V250 | MKG-V300 | MKG-V400 | MKG-V500 | MKG-V600
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 425/410/320 | 510/427/349 | 680/550/504 | 850/692/586 | 1020/820/670
|  | CFM | 250/241/188 | 300/251/205 | 400/324/297 | 500/407/345 | 600/483/394
Cooling | Capacity (H/M/L) | kW | 2.2/1.84/1.64 | 2.64/2.48/2.06 | 3.08/2.90/2.66 | 4.07/3.78/3.05 | 4.45/3.95/3.21
| Water flow rate | L/h | 378 | 454 | 530 | 700 | 765
| Water pressure drop | kPa | 23.1 | 33.6 | 42 | 34.9 | 36.3
Heating | Capacity (H/M/L) | kW | 3.02/2.85/2.35 | 3.69/2.92/2.49 | 4.34/3.77/3.35 | 5.69/4.14/3.63 | 6.30/5.17/4.18
| Water pressure drop | kPa | 22 | 31.4 | 40 | 29.7 | 32.8
Power input |  | W | 10.7 | 14.3 | 33 | 28 | 37.5
Sound pressure level (H/M/L) |  | dB(A) | 30/26/23 | 32/28/25 | 36/32/29 | 38/34/30 | 40/36/31
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Tangential fan | Tangential fan | Tangential fan | Tangential fan | Tangential fan
| Quantity |  | 1 | 1 | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
Net dimensions (W×H×D) |  | mm | 915×290×210 | 915×290×210 | 915×290×210 | 1070×315×210 | 1070×315×210
Packing size (W×H×D) |  | mm | 1020×385×300 | 1020×385×300 | 1020×385×300 | 1180×410×300 | 1180×410×300
Net weight |  | kg | 12 | 12 | 12 | 14.7 | 14.8
Gross weight |  | kg | 15.6 | 15.6 | 15.6 | 18.6 | 18.8
Water inlet/outlet pipe |  | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4
Drain pipe |  | mm | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20 | ODΦ20
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 50°C, entering air temperature 20°C DB, the same water flow as the cooling conditions. 3. Noise is tested in a semi-anechoic test room.

## H
Model |  |  | MKH3-V150 MKH4-V150 MKH5-V150 | MKH3-V250 MKH4-V250 MKH5-V250 | MKH3-V300 MKH4-V300 MKH5-V300 | MKH3-V400 MKH4-V400 MKH5-V400 | MKH3-V450 MKH4-V450 MKH5-V450 | MKH3-V500 MKH4-V500 MKH5-V500 | MKH3-V600 MKH4-V600 MKH5-V600 | MKH3-V800 MKH4-V800 MKH5-V800 | MKH3-V900 MKH4-V900 MKH5-V900
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 255/215/190 | 425/360/320 | 510/430/380 | 680/580/510 | 765/650/570 | 850/720/640 | 1020/870/765 | 1360/1160/1020 | 1530/1300/1150
|  | CFM | 150/125/110 | 250/210/190 | 300/250/220 | 400/340/300 | 450/380/335 | 500/420/375 | 600/510/450 | 800/680/600 | 900/760/675
External static pressure |  | Pa | H3 models: 12; H4/H5 models: 0
Cooling | Capacity (H/M/L) | kW | 1.15/0.87/0.69 | 1.87/1.50/1.20 | 2.53/1.97/1.45 | 3.27/2.60/1.86 | 3.97/2.88/2.61 | 4.85/3.61/2.61 | 5.64/4.01/3.06 | 6.52/5.29/4.00 | 7.85/6.08/4.92
| Water flow rate | L/h | 198 | 321 | 435 | 562 | 683 | 834 | 970 | 1121 | 1351
| Water pressure drop | kPa | 8.5 | 9.6 | 16.3 | 19.3 | 30.1 | 27.7 | 16.6 | 26.5 | 31.4
Heating | Capacity (H/M/L) | kW | 1.52/1.06/0.93 | 2.53/1.91/1.47 | 3.49/2.63/1.89 | 4.58/3.49/2.47 | 5.64/4.03/3.04 | 6.98/5.12/3.67 | 8.23/6.01/4.54 | 9.58/7.58/5.68 | 11.69/8.72/6.97
| Water pressure drop | kPa | 8 | 7.7 | 14.5 | 16.6 | 25.3 | 23.1 | 14.5 | 19.8 | 25.6
Power input |  | W | 14 | 16 | 29 | 33 | 29 | 35 | 39 | 70 | 116
Sound pressure level | H3 (H/M/L) | dB(A) | 29/25/19 | 30/26/20 | 32/28/22 | 34/30/24 | 36/32/26 | 38/33/27 | 40/34/28 | 41/35/29 | 43/37/31
| H4 (H/M/L) | dB(A) | 30/26/20 | 31/27/21 | 33/29/23 | 35/31/25 | 37/33/27 | 39/34/28 | 41/35/29 | 42/36/30 | 44/38/32
| H5 (H/M/L) | dB(A) | 29/25/19 | 30/26/20 | 32/28/22 | 34/30/24 | 36/32/26 | 38/33/27 | 40/34/28 | 41/35/29 | 43/37/31
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
Coil | Row |  | 3 | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body (H3 series) | Net dimensions (W×H×D) | mm | 550×545×212 | 550×545×212 | 750×545×212 | 750×545×212 | 950×545×212 | 950×545×212 | 1250×545×212 | 1250×545×212 | 1250×545×212
| Packing size (W×H×D) | mm | 639×639×305 | 639×639×305 | 839×639×305 | 839×639×305 | 1039×639×305 | 1039×639×305 | 1339×639×305 | 1339×639×305 | 1339×639×305
| Net weight | kg | 17 | 17 | 20 | 20 | 25 | 25 | 32 | 32 | 32
| Gross weight | kg | 19 | 19 | 23.5 | 23.5 | 29 | 29 | 36 | 36 | 36
Body (H4/H5 series) | Net dimensions (W×H×D) | mm | 800×592×220 | 800×592×220 | 1000×592×220 | 1000×592×220 | 1200×592×220 | 1200×592×220 | 1500×592×220 | 1500×592×220 | 1500×592×220
| Packing size (W×H×D) | mm | 889×683×312 | 889×683×312 | 1089×683×312 | 1089×683×312 | 1289×683×312 | 1289×683×312 | 1589×683×312 | 1589×683×312 | 1589×683×312
| Net weight | kg | 24.4 | 24.4 | 28.2 | 28.2 | 34.2 | 34.2 | 40 | 40 | 40
| Gross weight | kg | 28.4 | 28.4 | 33.2 | 33.2 | 39.7 | 39.7 | 45.5 | 45.5 | 45.5
Water inlet/outlet pipe |  | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4
Drain pipe |  | mm | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: Entering water 7℃, leaving water 12℃, Entering air temperature 27℃ DB/19℃ WB. Heating conditions: Entering water 50℃, the same water flow as the cooling conditions, Entering air temperature 20℃ DB. 3. Noise is tested in a semi-anechoic test room.

## AF
Model |  |  | MKA-V600F | MKA-V750F | MKA-V850F | MKA-V950F | MKA-V1200F | MKA-V1500F
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 1187/831/594 | 1233/863/617 | 1436/1005/718 | 1526/1068/763 | 1768/1238/884 | 1852/1323/945
|  | CFM | 700/489/350 | 726/508/363 | 845/592/423 | 898/629/449 | 1041/729/520 | 1112/779/556
Cooling | Capacity (H/M/L) | kW | 4.94/3.77/3.13 | 5.18/3.94/3.26 | 5.29/4.02/3.33 | 5.61/4.26/3.53 | 9.02/6.85/5.68 | 9.16/7.32/6.07
| Water flow rate | L/h | 850 | 891 | 910 | 965 | 1551 | 1576
| Water pressure drop | kPa | 15 | 12 | 12 | 15 | 70 | 72
Heating | Capacity (H/M/L) | kW | 7.14/5.42/4.5 | 7.41/5.64/4.67 | 7.88/5.99/4.97 | 8.24/6.26/5.19 | 11.31/8.59/7.12 | 11.88/9.28/7.69
| Water flow rate | L/h | 614 | 637 | 678 | 709 | 973 | 1022
| Water pressure drop | kPa | 40 | 42 | 45 | 49 | 63 | 71
Power input |  | W | 47 | 50 | 64 | 71 | 106 | 124
Sound pressure level |  | dB(A) | 40/31/25 | 42/34/26 | 43/34/27 | 45/35/29 | 46/37/32 | 48/39/33
Fan motor | Type |  | DC motor | DC motor | DC motor | DC motor | DC motor | DC motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades |  |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2 | 2 | 3 | 3
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7 | Φ7 | Φ7 | Φ7
Panel | Net dimensions (W×H×D) | mm | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950 | 950×45×950
| Packing size (W×H×D) | mm | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035 | 1035×90×1035
| Net weight | kg | 6 | 6 | 6 | 6 | 6 | 6
| Gross weight | kg | 9 | 9 | 9 | 9 | 9 | 9
Body | Net dimensions (W×H×D) | mm | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840 | 840×300×840
| Packing size (W×H×D) | mm | 900×330×900 | 900×330×900 | 900×330×900 | 900×307×900 | 900×330×900 | 900×330×900
| Net weight | kg | 27.5 | 27.5 | 27.5 | 27.5 | 30 | 30
| Gross weight | kg | 33.5 | 33.5 | 33.5 | 32.4 | 35 | 35
Pipe connections | Water inlet/outlet pipe | inch | Cold water: RC3/4; Hot water: RC1/2 |  |  | Cold water: RC3/4; Hot water: RC1/2
| Drain pipe | mm | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32 | ODΦ32
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 70°C, temperature drop 10°C DB, entering air temperature 20°C DB. 3. Noise is tested in a semi-anechoic test room.

## DF
Model |  |  | MKD-V300F | MKD-V400F | MKD-V500F
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 560/397/284 | 717/502/359 | 785/550/393
|  | CFM | 334/234/167 | 422/286/211 | 462/324/231
Cooling | Capacity (H/M/L) | kW | 2.39/1.82/1.46 | 2.88/2.19/1.8 | 3.24/2.46/2.04
| Water flow rate | L/h | 411 | 495 | 558
| Water pressure drop | kPa | 19.1 | 14.5 | 20.9
Heating | Capacity (H/M/L) | kW | 3.92/2.98/2.47 | 4.73/3.6/2.98 | 4.93/3.75/3.11
| Water flow rate | L/h | 337 | 407 | 424
| Water pressure drop | kPa | 20.5 | 29.1 | 34.5
Power input |  | W | 15 | 27 | 39
Sound pressure level |  | dB(A) | 34/26/20 | 36/28/22 | 40/31/25
Fan motor | Type |  | DC motor | DC motor | DC motor
| Quantity |  | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 1
Coil | Row |  | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ7 | Φ7 | Φ7
Panel | Net dimensions (W×H×D) | mm | 647×50×647 | 647×50×647 | 647×50×647
| Packing size (W×H×D) | mm | 715×123×715 | 715×123×715 | 715×123×715
| Net weight | kg | 2.5 | 2.5 | 2.5
| Gross weight | kg | 4.5 | 4.5 | 4.5
Body | Net dimensions (W×H×D) | mm | 575×261×575 | 575×261×575 | 575×261×575
| Packing size (W×H×D) | mm | 670×290×670 | 670×290×670 | 670×290×670
| Net weight | kg | 16.7 | 16.7 | 16.7
| Gross weight | kg | 22.7 | 22.7 | 22.7
Pipe connections | Water inlet/outlet pipe | inch | Cold water: G3/4; Hot water: G1/2
| Drain pipe | mm | ODΦ25 | ODΦ25 | ODΦ25
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: entering water 7°C, temperature rise 5°C, entering air temperature 27°C DB/19°C WB. Heating conditions: entering water 70°C, temperature drop 10°C DB, entering air temperature 20°C DB. 3. Noise is tested in a semi-anechoic test room.

## T3F
Model MKT3- |  |  | V200F | V300F | V400F | V500F | V600F | V800F | V1000F | V1200F
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 320/210/140 | 450/340/280 | 530/390/260 | 690/470/370 | 900/670/440 | 1240/840/670 | 1610/1160/790 | 1850/1400/970
|  | CFM | 190/120/85 | 270/200/170 | 320/230/160 | 410/280/220 | 530/400/260 | 730/500/400 | 950/690/470 | 1090/830/570
Standard external static pressure |  | Pa | 12Pa (default); 30/50Pa can be set through dial switch on PCB.
Cooling | Capacity (H/M/L) | kW | 1.4/1.1/0.8 | 2.2/1.7/1.5 | 2.5/2.0/1.5 | 3.0/2.4/1.9 | 4.2/3.5/2.5 | 5.3/4.1/3.1 | 6.7/5.4/3.9 | 8.2/6.5/4.6
| Water flow rate | L/h | 270 | 380 | 470 | 540 | 730 | 930 | 1180 | 1400
| Water pressure drop | kPa | 10.2 | 10.5 | 11.3 | 13.6 | 15.3 | 12.8 | 21.6 | 34.9
Heating | Capacity (H/M/L) | kW | 2.1/1.7/1.4 | 3.0/2.6/2.1 | 3.7/3.2/2.5 | 4.4/3.6/3.0 | 5.7/4.8/3.4 | 6.8/5.5/4.6 | 8.2/6.9/5.2 | 10.1/8.6/6.8
| Water pressure drop | kPa | 8.9 | 9.1 | 10.1 | 11.7 | 12.7 | 12.0 | 15.5 | 25.73
Power input |  | W | 14 | 19 | 24 | 36 | 45 | 57 | 87 | 95
Sound pressure level | 12Pa (H/M/L) | dB(A) | 35/25/23 | 36/29/23 | 38/32/24 | 43/35/27 | 46/39/30 | 46/38/30 | 48/41/31 | 47/40/30
| 30Pa (H/M/L) | dB(A) | 41/32/25 | 39/30/25 | 44/38/28 | 46/37/30 | 49/41/33 | 49/43/33 | 49/42/33 | 50/42/34
| 50Pa (H/M/L) | dB(A) | 43/34/26 | 44/36/26 | 47/41/28 | 48/42/33 | 51/44/39 | 52/45/37 | 51/44/35 | 53/45/37
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 2 | 2 | 2 | 2 | 4 | 4 | 4
Coil | Row |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Max. Working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Net Dimensions (W×H×D) |  | mm | 741×241×522 | 841×241×522 | 941×241×522 | 941×241×522 | 1161×241×522 | 1461×241×522 | 1566×241×522 | 1856×241×522
Packing size (W×H×D) |  | mm | 790×260×550 | 890×260×550 | 990×260×550 | 990×260×550 | 1210×260×550 | 1510×260×550 | 1615×260×550 | 1905×260×550
Net weight |  | kg | 17.2 | 19.5 | 21.5 | 21.5 | 24.2 | 33.5 | 35.2 | 39.7
Gross weight |  | kg | 20.2 | 22.5 | 24.5 | 24.5 | 27.7 | 37.7 | 39.7 | 44.9
Water inlet/outlet pipe |  | inch | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4 | RC3/4
Drain pipe |  | inch | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4 | R3/4