## H
Model |  |  | MKH3-V150 MKH4-V150 MKH5-V150 | MKH3-V250 MKH4-V250 MKH5-V250 | MKH3-V300 MKH4-V300 MKH5-V300 | MKH3-V400 MKH4-V400 MKH5-V400 | MKH3-V450 MKH4-V450 MKH5-V450 | MKH3-V500 MKH4-V500 MKH5-V500 | MKH3-V600 MKH4-V600 MKH5-V600 | MKH3-V800 MKH4-V800 MKH5-V800 | MKH3-V900 MKH4-V900 MKH5-V900
Power supply |  | V/Ph/Hz | 220-240/1/50
Air flow (H/M/L) |  | m3/h | 255/215/190 | 425/360/320 | 510/430/380 | 680/580/510 | 765/650/570 | 850/720/640 | 1020/870/765 | 1360/1160/1020 | 1530/1300/1150
|  | CFM | 150/125/110 | 250/210/190 | 300/250/220 | 400/340/300 | 450/380/335 | 500/420/375 | 600/510/450 | 800/680/600 | 900/760/675
External static pressure |  | Pa | H3 models: 12; H4/H5 models: 0
Cooling | Capacity (H/M/L) | kW | 1.15/0.87/0.69 | 1.87/1.50/1.20 | 2.53/1.97/1.45 | 3.27/2.60/1.86 | 3.97/2.88/2.61 | 4.85/3.61/2.61 | 5.64/4.01/3.06 | 6.52/5.29/4.00 | 7.85/6.08/4.92
| Water flow rate | L/h | 198 | 321 | 435 | 562 | 683 | 834 | 970 | 1121 | 1351
| Water pressure drop | kPa | 8.5 | 9.6 | 16.3 | 19.3 | 30.1 | 27.7 | 16.6 | 26.5 | 31.4
Heating | Capacity (H/M/L) | kW | 1.52/1.06/0.93 | 2.53/1.91/1.47 | 3.49/2.63/1.89 | 4.58/3.49/2.47 | 5.64/4.03/3.04 | 6.98/5.12/3.67 | 8.23/6.01/4.54 | 9.58/7.58/5.68 | 11.69/8.72/6.97
| Water pressure drop | kPa | 8 | 7.7 | 14.5 | 16.6 | 25.3 | 23.1 | 14.5 | 19.8 | 25.6
Power input |  | W | 14 | 16 | 29 | 33 | 29 | 35 | 39 | 70 | 116
Sound pressure level | H3 (H/M/L) | dB(A) | 29/25/19 | 30/26/20 | 32/28/22 | 34/30/24 | 36/32/26 | 38/33/27 | 40/34/28 | 41/35/29 | 43/37/31
| H4 (H/M/L) | dB(A) | 30/26/20 | 31/27/21 | 33/29/23 | 35/31/25 | 37/33/27 | 39/34/28 | 41/35/29 | 42/36/30 | 44/38/32
| H5 (H/M/L) | dB(A) | 29/25/19 | 30/26/20 | 32/28/22 | 34/30/24 | 36/32/26 | 38/33/27 | 40/34/28 | 41/35/29 | 43/37/31
Fan motor | Type |  | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor | DC Motor
| Quantity |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Fan | Type |  | Centrifugal, forward-curved Blades
| Quantity |  | 1 | 1 | 2 | 2 | 2 | 2 | 3 | 3 | 3
Coil | Row |  | 3 | 3 | 2 | 2 | 3 | 3 | 2 | 2 | 2
| Max. working pressure | MPa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| Diameter | mm | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52 | Φ9.52
Body (H3 series) | Net dimensions (W×H×D) | mm | 550×545×212 | 550×545×212 | 750×545×212 | 750×545×212 | 950×545×212 | 950×545×212 | 1250×545×212 | 1250×545×212 | 1250×545×212
| Packing size (W×H×D) | mm | 639×639×305 | 639×639×305 | 839×639×305 | 839×639×305 | 1039×639×305 | 1039×639×305 | 1339×639×305 | 1339×639×305 | 1339×639×305
| Net weight | kg | 17 | 17 | 20 | 20 | 25 | 25 | 32 | 32 | 32
| Gross weight | kg | 19 | 19 | 23.5 | 23.5 | 29 | 29 | 36 | 36 | 36
Body (H4/H5 series) | Net dimensions (W×H×D) | mm | 800×592×220 | 800×592×220 | 1000×592×220 | 1000×592×220 | 1200×592×220 | 1200×592×220 | 1500×592×220 | 1500×592×220 | 1500×592×220
| Packing size (W×H×D) | mm | 889×683×312 | 889×683×312 | 1089×683×312 | 1089×683×312 | 1289×683×312 | 1289×683×312 | 1589×683×312 | 1589×683×312 | 1589×683×312
| Net weight | kg | 24.4 | 24.4 | 28.2 | 28.2 | 34.2 | 34.2 | 40 | 40 | 40
| Gross weight | kg | 28.4 | 28.4 | 33.2 | 33.2 | 39.7 | 39.7 | 45.5 | 45.5 | 45.5
Water inlet/outlet pipe |  | inch | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4 | G3/4
Drain pipe |  | mm | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16 | ODΦ16
Notes: 1. H: High fan speed; M: Medium fan speed; L: Low fan speed. 2. Cooling conditions: Entering water 7℃, leaving water 12℃, Entering air temperature 27℃ DB/19℃ WB. Heating conditions: Entering water 50℃, the same water flow as the cooling conditions, Entering air temperature 20℃ DB. 3. Noise is tested in a semi-anechoic test room.