## 大冷霸
Model MKA- |  |  |  | V600F | V750F | V850F | V950F | V1200F | V1500F
Air flow |  | H/M/L | m3/h | 1187/831/594 | 1233/863/617 | 1436/1005/718 | 1526/1068/763 | 1768/1238/884 | 1852/1323/945
|  | H/M/L | CFM | 700/489/350 | 726/508/363 | 845/592/423 | 898/629/449 | 1041/729/520 | 1112/779/556
Cooling | Capacity | H/M/L | kW | 4.94/3.77/3.13 | 5.18/3.94/3.26 | 5.29/4.02/3.33 | 5.61/4.26/3.53 | 9.02/6.85/5.68 | 9.16/7.32/6.07
| Water flow rate | H | l/h | 850 | 891 | 910 | 965 | 1551 | 1576
| Water pressure drop | H | kPa | 15 | 12 | 12 | 15 | 70 | 72
Heating 70℃ | Capacity | H/M/L | kW | 7.14/5.42/4.5 | 7.41/5.64/4.67 | 7.88/5.99/4.97 | 8.24/6.26/5.19 | 11.31/8.59/7.12 | 11.88/9.28/7.69
| Water flow rate | H | l/h | 614 | 637 | 678 | 709 | 973 | 1022
| Water pressure drop | H | kPa | 40 | 42 | 45 | 49 | 63 | 71
Power supply |  |  | V/Ph/Hz | 220-240/1/50 |  |  | 220-240/1/50
Power input |  | H | W | 47 | 50 | 64 | 71 | 106 | 124
Sound pressure level |  | H/M/L | dB(A) | 40/31/25 | 42/34/26 | 43/34/27 | 45/35/29 | 46/37/32 | 48/39/33
Fan motor | Type |  |  | DC motor |  |  | DC motor
| Quantity |  |  | 1 |  |  | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades |  |  | Centrifugal, forward-curved Blades
| Quantity |  |  | 1 |  |  | 1
Coil | Row |  |  | 2 | 2 | 2 | 2 | 3 | 3
| Max. Working pressure |  | MPa | 1.6 |  |  | 1.6
| Coil length x height |  | mm | 1990x252 |  |  | 1990x252 | 2050x252 | 2080x252
| Fin type |  |  | Hydrophilic aluminium |  |  | Hydrophilic aluminium
| Number of circuits |  |  | Cool 9; Heat 3 |  |  | Cool 9;Heat 3 | Cool 14; Heat 4
| Fin spacing |  | mm | 1.5 |  |  | 1.5
| Diameter |  | mm | Φ7 |  |  | Φ7
Panel | Dimensions | W×H×D | mm | 950×45×950 |  |  | 950×45×950
| Packing | W×H×D | mm | 1035×90×1035 |  |  | 1035×90×1035
| Net weight |  | kg | 6 |  |  | 6
| Gross weight |  | kg | 9 |  |  | 9
Body | Dimensions | W×H×D | mm | 840×300×840 |  |  | 840×300×840
| Packing | W×H×D | mm | 900×330×900 |  |  | 900×307×900
| Net weight |  | kg | 27.5 | 27.5 | 27.5 | 27.5 | 30 | 30
| Gross weight |  | kg | 33.5 | 33.5 | 33.5 | 32.4 | 35 | 35
Pipe connection | Water inlet/outlet pipe |  | Inch | Cold water: RC3/4; Hot water: RC1/2 |  |  | Cold water: RC3/4; Hot water: RC1/2
| Drain pipe |  | mm | ODΦ32

## 小冷霸
Model MKD- |  |  |  | V300F | V400F | V500F
Air flow |  | H/M/L | m3/h | 560/397/284 | 717/502/359 | 785/550/393
|  | H/M/L | CFM | 334/234/167 | 422/286/211 | 462/324/231
Cooling | Capacity | H/M/L | kW | 2.39/1.82/1.46 | 2.88/2.19/1.8 | 3.24/2.46/2.04
| Water flow rate | H | l/h | 411 | 495 | 558
| Water pressure drop | H | kPa | 19.1 | 14.5 | 20.9
Heating 70℃ | Capacity | H/M/L | kW | 3.92/2.98/2.47 | 4.73/3.6/2.98 | 4.93/3.75/3.11
| Water flow rate | H | l/h | 337 | 407 | 424
| Water pressure drop | H | kPa | 20.5 | 29.1 | 34.5
Power supply |  |  | V/Ph/Hz | 220-240/1/50
Power input |  | H | W | 15 | 27 | 39
Sound pressure level |  | H/M/L | dB(A) | 34/26/20 | 36/28/22 | 40/31/25
Fan motor | Type |  |  | DC motor
| Quantity |  |  | 1
Fan | Type |  |  | Centrifugal, forward-curved Blades
| Quantity |  |  | 1
Coil | Row |  |  | 2
| Max. Working pressure |  | MPa | 1.6
| Coil length x height |  | mm | 1315x210
| Fin spacing |  | mm | 1.3
| Fin type |  |  | Hydrophilic aluminium
| Number of circuits |  |  | Cool 3; Heat 3 | Cool 4;Heat 3 | Cool 4;Heat 3
| Diameter |  | mm | Φ7
Panel | Dimensions | W×H×D | mm | 647×50×647
| Packing | W×H×D | mm | 715×123×715
| Net weight |  | kg | 2.5
| Gross weight |  | kg | 4.5
Body | Dimensions | W×H×D | mm | 575×261×575
| Packing | W×H×D | mm | 675×320×675
| Net weight |  | kg | 16.7
| Gross weight |  | kg | 22.7
Pipe connection | Water inlet/outlet pipe |  | Inch | Cold water: G3/4; Hot water: G1/2
| Drain pipe |  | mm | ODΦ25